## GISAGARA
GISAGARA
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-010 | PTR-1-010
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GSGR-039 | GSGR-039
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | CHINA ZUTCO | CHINA ZUTCO
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2021 | 2021
| Year_commissioning | Short Integer | 2021 | 2021
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/30kV | 2
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 20MVA | 20
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 30kV | 30
| TertiaryCurrent_A | Short Integer | 0 | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 52.5A | 52.5
| SecondaryCurrent_A | Double | 385.3A | 385.3
| TertiaryCurrent_A | Double | 0 | 0
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 0.11 | 0.11
| NoLoadCurr_Percentage | Double | 0.1 | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 10kW | 10
| LoadLosses | Double | 55kW | 55
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 17 | 17
| TapChangerType | Short Integer | Onload | 1
| TapChangerModel | Text | CM2III 500Y/72.5C-10193W | CM2III 500Y/72.5C-10193W
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | SMS | SMS
| Tap_changer_country_orgin_ | Text | CHINA | CHINA
| TapChangerManufacturingDate | Short Integer | 2021 | 2021
| SerialNumber | Text | CM2200011 | CM2200011
| Barcode | Text | NA | NA
| TotalWeight | Double | 83640 | 83640
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 29300 | 29300
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Polcelain | 1
Earthing Transformer | transfomerID | Text | ETR-1-010 | ETR-1-010
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GSGR-039 | GSGR-039
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | ZHE -JIANGSHAN TRANSFRMER CO.LTD | ZHE -JIANGSHAN TRANSFRMER CO.LTD
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2021 | 2021
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 30/0.4kV | 1
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 0.315MVA | 0.315
| Primaryvoltage__kv | Double | 30kV | 30
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 6A | 6
| SecondaryCurrent_A | Double | 455.2A | 455.2
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNz5 | 16
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 0.4 | 0.4
| No_Load_losses | Double | 0.9kW | 0.9
| LoadLosses | Double | 4.5kW | 4.5
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 5 | 5
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | Onload | Onload
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | ZHE -JIANGSHAN TRANSFRMER CO.LTD | ZHE -JIANGSHAN TRANSFRMER CO.LTD
| Tap_changer_country_orgin_ | Text | CHINA | CHINA
| TapChangerManufacturingDate | Short Integer | 2021 | 2021
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 4540kg | 4540
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 1385kg | 1385
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 630A | 630
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2021 | 2021
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | GSGR-039 | GSGR-039
| Busbar_HV_ID | Text | BB-010 | BB-010
| Number_of_Busbar_HV | Short Integer | 1 | 1
| Number_of_Busbar_MV | Short Integer | 1 | 1
| Type_of_Busbar | Short Integer | 2xString Conductor ACSR 240/40mm2 | 2xString Conductor ACSR 240/40mm2
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | Aluminium | 1
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 220kV | 220
| Short_circuit_current_kA | Double | 40kA | 40
| Nominal_Current_A | Double | 908A | 908
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-039 | SWG-039
| Substation_ID | Text | GSGR-039 | GSGR-039
| FeederID | Text | H01 | H01
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Incomer Feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021 | 2021
| Serial_Number | Text | CV966736-000020/1 | CV966736-000020/1
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2021 | 2021
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000m
| Nominal_voltage_kV | Double | 30kV | 30
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIEMENS - 7SA82 | SIEMENS - 7SA82
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-010 | SWG-039
| Substation_ID | Text | GSGR-010 | GSGR-039
| FeederID | Text | H02 | H02
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021 | 2021
| Serial_Number | Text | CV966736-000030/1 | CV966736-000030/1
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2021 | 2021
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30kV | 30
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIEMENS - 7SA82 | SIEMENS - 7SA82
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-010 | SWG-039
| Substation_ID | Text | GSGR-010 | GSGR-039
| FeederID | Text | H03 | H03
| FeederName | Text | HUYE | HUYE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021 | 2021
| Serial_Number | Text | CV966736-000040/1 | CV966736-000040/1
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2021 | 2021
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30kV | 30
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIEMENS - 7SA82 | SIEMENS - 7SA82
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-010 | SWG-039
| Substation_ID | Text | GSGR-010 | GSGR-039
| FeederID | Text | H04 | H04
| FeederName | Text | SAVE | SAVE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021 | 2021
| Serial_Number | Text | CV966736-000050/1 | CV966736-000050/1
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2021 | 2021
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30kV | 30
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIEMENS - 7SA82 | SIEMENS - 7SA82
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-010 | SWG-039
| Substation_ID | Text | GSGR-010 | GSGR-039
| FeederID | Text | H05 | H05
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021 | 2021
| Serial_Number | Text | CV966736-000060/1 | CV966736-000060/1
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2021 | 2021
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30kV | 30
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIEMENS - 7SA82 | SIEMENS - 7SA82
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-010 | SWG-039
| Substation_ID | Text | GSGR-010 | GSGR-039
| FeederID | Text | H06 | H06
| FeederName | Text | BUSBAR VT | BUSBAR VT
| PanelFunction | Short Integer | Bus bar Feeder | 3
| SwitchingDevices | Short Integer | Isolator only | 1
| Type_of_MV_cable_termination | Short Integer | NA | NA
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021 | 2021
| Serial_Number | Text | CV966736-000070/1 | CV966736-000070/1
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2021 | 2021
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30kV | 30
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIEMENS - 7SA82 | SIEMENS - 7SA82
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | D01 | D01
| Substation_ID | Text | GSGR-010 | GSGR-039
| Line_Bay_Name | Text | KIGOMA | KIGOMA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 40MVA | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | ABB-RED670 | ABB-RED670
| Type_of_Distance_relay | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | Including in RED 670 | Including in RED 670
| Type_of_BCU_Bay_control_unit | Text | SIEMENS-6MD85 | SIEMENS-6MD85
Line Bay | Line_Bay_ID | Text | D02 | D02
| Substation_ID | Text | GSGR-010 | GSGR-039
| Line_Bay_Name | Text | NGOZI | NGOZI
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 40MVA | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | ABB-RED 670 | ABB-RED 670
| Type_of_Distance_relay | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | Including in RED 670 | Including in RED 670
| Type_of_BCU_Bay_control_unit | Text | SIEMENS-6MD85 | SIEMENS-6MD85
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1 | VT2-1
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2 | VT2-2
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3 | VT2-3
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-1 | VT4-1
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-2 | VT4-2
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-3 | VT4-3
| Substation_ID | Text | GSGR-010 | GSGR-039
| Manufacturer | Text | MEHRU EME | MEHRU EME
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV | 220kV
| HighestSystemVoltage_kV | Double | 245kV | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA | 75
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC8344/1/1/21 | OC8344/1/1/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC8344/1/4/21 | OC8344/1/4/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC8344/1/5/21 | OC8344/1/5/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT2-1 | CT2-1
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC 8344/7/1/21 | OC 8344/7/1/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT2-2 | CT2-2
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC 8344/7/6/21 | OC 8344/7/6/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT2-3 | CT2-3
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40VA
| Primaryvoltage__kv | Double | 220kV | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50Hz
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 40VA | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100kA
| KneePoint_V | Double
| SerialNumber | Text | OC 11606/1/1/21 | OC 11606/1/1/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275kV
| Insulator | Short Integer | Oil | Oil
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC8344/2/3/21 | OC8344/2/3/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | OC8344/2/2/21 | OC8344/2/2/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | MEHRU EME | MEHRU EME
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | GSGR-010 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double
| SerialNumber | Text | 0C8344/2/1/21 | 0C8344/2/1/21
| SF_ALF | Text | 20 | 20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D | GE T&D
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | GSGR-010 | GSGR-010
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | "32710051390010001 | "32710051390010001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D | GE T&D
| CircuitBreakerID | Text | CB2 | CB2
| Substation_ID | Text | GSGR-010 | GSGR-010
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | "32710051390010002 | "32710051390010002
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D | GE T&D
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | GSGR-010 | GSGR-010
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | '327005139010001 | '327005139010001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1
| Substation | Text | GSGR-010 | GSGR-010
| Type | Short Integer | 1
| FunctionType | Short Integer | 1
| Manufacturer | Text | GE /Suzhou
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES
| Motor_Type | Short Integer | DC
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | GSGR-010 | GSGR-010
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 2 | 2
| Manufacturer | Text | GE /Suzhou | GE /Suzhou
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2 | Q1-2
| Substation | Text | GSGR-010 | GSGR-010
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | GE /Suzhou | GE /Suzhou
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2 | Q9-2
| Substation | Text | GSGR-010 | GSGR-010
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 2 | 2
| Manufacturer | Text | GE /Suzhou | GE /Suzhou
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3 | Q1-3
| Substation | Text | GSGR-010 | GSGR-010
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | GE /Suzhou | GE /Suzhou
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing | Not existing
| Substation_ID | Text | Not existing | Not existing
| CountryOfManufacturer | Text | Not existing | Not existing
| Applicable_Standard | Text | Not existing | Not existing
| Model | Text | Not existing | Not existing
| RatedPoweratAmbientTemp | Double | Not existing | Not existing
| PowerSupply | Text | Not existing | Not existing
| ActivePower_Min_kW | Double | Not existing | Not existing
| TypeofCooling | Short Integer | Not existing | Not existing
| Protection_class_cubicle | Text | Not existing | Not existing
| Rated_DC_VoltageInput | Double | Not existing | Not existing
| RatedVoltageOutput | Double | Not existing | Not existing
| Frequency_Hz | Short Integer | Not existing | Not existing
| Maximum_power_loss_rated_load | Double | Not existing | Not existing
| Total_Weight | Double | Not existing | Not existing
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | GISAGARA | 10
| Substation_ID | Text | GSGR-039 | GSGR-039
| Substation_Total_Capacity_MVA | Double | 20MVA | 20
| Substation_Voltage_Level_kV | Short Integer | 220/30kV | 13
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 1 | 1
| Numbe_of_Earthing_Transfomer | Short Integer | 1 | 1
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | YES | 1
| Busbar_Configuration_HV | Short Integer | Single busbar | 1
| Number of MV Feeders | Short Integer | 6 | 6
| Number of HV line Bays | Short Integer | 2 | 2
| Number of Trx Bays | Short Integer | 1 | 1
| Configuration_Busbar_MV | Short Integer | Double busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2008 | 2020
| Year_of_upgrade | Short Integer | NA | 0
| Contractor_Name | Text | NCC | NCC
| Substation_Meter_SN | Text | NA | Not Existing
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1200 | NPT1200
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | MKGW-025 | MKGW-025
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-1 | SA2-1
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-2 | SA2-2
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-3 | SA2-3
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-1 | SA3-1
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-2 | SA3-2
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2020 | 2020
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550 | 550
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 1200 | 1200
| PowerFrequencyWithstandVol | Double | 550 | 550
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | HBL | HBL
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| Type | Short Integer | 1 | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| BatteryFloatingVoltage | Double | 50 | 50
| RatedVoltage | Double | 48 | 48
| TenHrsRatingCapacity | Double | 80 | 80
| One_min_rating_Current_A | Double | 800 | 800
| MaximumVolatge_V | Double | 55.2 | 55.2
| MinimumVoltage_V | Double | 40.8 | 40.8
| MinimumVoltageperCell | Double | 1.02 | 1.02
| NumberofCells | Short Integer | 40 | 40
| BatteryFloatingVoltage | Double | 53.9 | 53.9
| BoostChargingVoltage | Double | 55.8 | 55.8
| FloatChargeCurrent_A | Double | 6.2 | 6.2
| BoostChargeCurrent | Double | 60 | 60
| SelfDischargeat_25oC | Double | 0.7 | 0.7
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 8 | 8
DC Supply 110 VDC Battery | Manufacturer | Text | HBL | HBL
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| Model | Text | 88 KBL | 88 KBL
| Type | Short Integer | 1 | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110 | 110
| TenHrsRatingCapacity | Double | 255 | 255
| One_min_rating_Current_A | Double | 100 | 100
| MaximumVolatge_V | Double | 136.4 | 136.4
| MinimumVoltage_V | Double | 88 | 88
| MinimumVoltageperCell | Double | 1 | 1
| Number_of_cells__No_ | Long Integer | 88 | 88
| BatteryFloatingVoltage | Double | 126 | 126
| BoostChargingVoltage | Double | 123.3 | 123.3
| FloatChargeCurrent_A | Double | 6.2 | 6.2
| BoostChargeCurrent | Double | 100 | 100
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | HBL power system Ltd | HBL power system Ltd
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| Model | Text
| Charger_type | Short Integer | 2 | 2
| Standards_ | Short Integer | DIN VDE 0558 | DIN VDE 0558
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 230 | 230
| Rated_InputPower_kVA | Double | 5.53 | 5.53
| DC Output (Kw) | Double | 2.88 | 2.88
| DC_Output_kV | Double | 48 | 48
| Rated_output_Voltage_V | Double | 48 | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5 | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000 | 2000
| Degree_protection_ | Short Integer | 55 | 55
| DCDistributionBoard | Short Integer | 0 | 0
| RatedCurrent_A | Double
| NumberofFeeders | Short Integer
| short_circuit_capacity_breaker | Double
DC Supply 110 VDC charger | Manufacturer | Text | HBL power system Ltd | HBL power system Ltd
| Substation_ID | Text | GSGR-039 | GSGR-039
| CountryOfManufacturer | Text | INDIA | INDIA
| Model | Text
| TypeofOperation | Short Integer | 1 | 1
| Charger_type | Short Integer | 2 | 2
| Standards_ | Text | DIN VDE 0558 | DIN VDE 0558
| ChargingTime | Double | 5 | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400 | 400
| Rated_InputPower_kVA | Double | 14.8 | 14.8
| VoltageVariation | Double
| DC_Output_kV | Double | 110 | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110 | 110
| MaximumDC_Voltage_V | Double | 126 | 126
| ConstantVoltageAccuracy | Double
| Rated_DC_output_Current_A | Double | 130A | 130A
| FloatingVoltageRegulatin | Double | 104.4 | 104.4
| EqualisingVoltageRegulatin | Double | 128.8 | 128.8
| Minimum_Insulation_resistance_ | Double | 5 | 5
| TypeofCooling | Short Integer
| Ambient_temperature | Double
| Altitude_m | Double | 1000 | 1000
| Total_Weight_Charger_kg | Double | 340 | 340
| Degree_protection_ | Short Integer | 55 | 55
| RatedCurrent_A | Double | 100 | 100
| ShortCircuitStrength_kA_sec | Double
| BusbarMaterial | Short Integer
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE | FRANCE
| Type | Text | REASON DR60 | REASON DR60
| Standards | Text | IEC61850 | IEC61850
| Arrangement | Short Integer | 2 | 2
| VT_CT_Connection | Short Integer | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| Nominal_input_current_A | Double | 1 | 1
| Nominal_voltage_Vdc | Double | 110 | 110
| Power_consumption_VA | Double | 150 | 150
| NumberofAnalogInputs | Short Integer | 32 | 32
| NumberofBinaryInputs | Short Integer | 96 | 96
| NumberofBinaryOutputs | Short Integer | 48 | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | KIGOMA | KIGOMA
| Year_of_commisioning | Short Integer | 2020 | 2020
| ContractorName | Text | NCC | NCC
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 6 | 6
| ShieldWire | Short Integer | 1 | 1
| ConductorType | Short Integer | 1 | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 4104 | 41.4
| CurrentCarryingCapacity | Double | 80 | 80
| NominalBreakingLoad_KN | Double | 130 | 130
| MaxElectricResitance | Double | 0.119 | 0.119
| PositiveSequenceReactance | Double | 0.427 | 0.427
| PositiveSequenceResistance | Double | 0.123 | 0.123
| ZeroSequenceResistance | Double | 0.327 | 0.327
| ZeroSequenceReactance | Double | 1.119 | 1.119
| ZeroSequenceCapacitance | Double | 0.011 | 0.011
| PositiveSequenceCapacitance | Double | 0.0066 | 0.0066
High Voltage Line | Name | Text | NGOZI | NGOZI
| Year_of_commisioning | Short Integer | 2020 | 2020
| ContractorName | Text | ELTEL | ELTEL
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 6 | 6
| ShieldWire | Short Integer | 1 | 1
| ConductorType | Short Integer | 1 | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 23.2 | 23.2
| CurrentCarryingCapacity | Double | 40 | 40
| NominalBreakingLoad_KN | Double | 130 | 130
| MaxElectricResitance | Double | 0.119 | 0.119
| PositiveSequenceReactance | Double | 0.427 | 0.427
| PositiveSequenceResistance | Double | 0.123 | 0.123
| ZeroSequenceResistance | Double | 0.327 | 0.327
| ZeroSequenceReactance | Double | 1.119 | 1.119
| ZeroSequenceCapacitance | Double | 0.011 | 0.011
| PositiveSequenceCapacitance | Double | 0.0066 | 0.0066
Transformer Bay | Trx_Bay_ID | Text | D03 | D03
| Substation_ID | Text | GSGR-039 | GSGR-039
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 1 | 1
| Trx_Bay_Capacity_MVA | Double | 20 | 20
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_Trx_Differencial_relay | Text | ABB-RET670 | ABB-RET670
| Type_of_Back_up_relay | Text | SIEMENS -7UT86 | SIEMENS -7UT86
| Type_of_BCU_Bay_control_unit | Text | SIEMENS - 6MD85 | SIEMENS - 6MD85
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SIEMENS | SIEMENS
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 3HA49 | 3HA49
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | 1 | 1
| ArcQuenchingMedium | Short Integer | 2 | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 15 | 15
| MaxContinuousOperatVolt_kV | Double | 24 | 24
| RatedImpulseWithstandVol | Double | 95 | 95
| PowerFrequencyWithstandVol | Double | 38 | 38
| Rated_Frequency | Short Integer | 50 | 50
| Rated_short_time_withstand_current__kA_ | Text | 25 | 25
| Rated_Peak_Short_Cir_Current | Double | 63 | 63
| RatedNormalCurrent_A | Double | 1250 | 1250
| RatedShortCircuitBreakCur_kA | Double | 25 | 25
| RatedShortCircuitMakCurrent_A | Double | 63 | 63
| RatedCableChargingBreakingCur | Double | 50 | 50
| MaximumCApacitivBreakingCur | Double | 875 | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60 | 60
| DeadTime_ms | Double | 300 | 300
| BreakTime_ms | Double | 85 | 85
| MakeTime_ms | Double | 70 | 70
| ArcingTime_ms | Double | 15 | 15
| AtRAtedContinuousCurrent | Double
| AtRAtedBreakingCurrent | Double
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110 | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110 | 110
| PowerSupply | Short Integer | 110 | 110
| HandOperatingFacility | Short Integer | 1 | 1
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV1 | CT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 30 | 30
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 500 | 500
| Rated_Secondary_Current | Double | 1 | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 95kV | 95
| LimitsContPrimaryCurrency_A | Double | 2400 | 2400
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV3 | CT-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 30 | 30
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300 | 300
| Rated_Secondary_Current | Double | 1 | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10 | 10
| RatedShortTimeWithstandCur | Double | 25 | 25
| Rated_Peak_Short_Cir_Current | Double | 63 | 63
| RatedImpulseWithstandVol | Double | 170 | 170
| LimitsContPrimaryCurrency_A | Double | 768 | 768
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV1 | VT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 70 | 70
| RatedImpulseWithstandVol | Double | 170 | 170
| RatedPrimaryVoltage_kV | Double | 30 | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 110 | 110
| Rated_secondary_voltage_winding_2__V_ | Text | 100 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60 | 60
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV2 | VT-MV2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 70 | 70
| RatedImpulseWithstandVol | Double | 170 | 170
| RatedPrimaryVoltage_kV | Double | 30 | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 110 | 110
| Rated_secondary_voltage_winding_2__V_ | Text | 100 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60 | 60
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV3 | VT-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 70 | 70
| RatedImpulseWithstandVol | Double | 170 | 170
| RatedPrimaryVoltage_kV | Double | 30 | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 100 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60 | 60
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-1-039 | TSP-CPR-1-039
| Substation_ID | Text | GSGR-039 | GSGR-039
| Bay_ID | Text | D01 | D01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5 | 2.5
| Max_height_mm | Double | 2000 | 2000
| MaxWidth_mm | Double | 1500 | 1500
| MaxDepth | Double | 2500 | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | ABB-RED670 | ABB-RED670
Distance Protection | RelayType | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Bay_ID | Text | D01 | D01
| Substatoin_ID | Text | GSGR-039 | GSGR-039
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1 | 1
| Rated_Voltage | Double | 100 | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110 | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-2-039 | TSP-CPR-2-039
| Substation_ID | Text | GSGR-039 | GSGR-039
| Bay_ID | Text | D02 | D02
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5 | 2.5
| Max_height_mm | Double | 2000 | 2000
| MaxWidth_mm | Double | 1500 | 1500
| MaxDepth | Double | 2500 | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | ABB-RED670 | ABB-RED670
Distance Protection | RelayType | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | GSGR-039 | GSGR-039
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1 | 1
| Rated_Voltage | Double | 100 | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110 | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Standby Generator | Manufacturer | Text | CUMMINS POWER GENERATION | CUMMINS POWER GENERATION
| Substation_ID | Text | GSGR-039 | GSGR-039
| Standby_Generator_ID | Text | DGU-1-039 | DGU-1-039
| CountryOfManufacturer | Text | INDIA | INDIA
| Mode_Operation | Short Integer
| Model | Text | C66D5L | C66D5L
| Type_Assembly | Short Integer
| Arrangement | Short Integer
| Phases | Short Integer | 3 | 3
| RatedOuptuPower_kVA | Double | 250 | 250
| RatedVoltage | Double | 400 | 400
| RatedCurrent_A | Double | 360 | 360
| PowerFactor | Double | 0.8 | 0.8
| CouplingofEngine | Text | Direct | Direct
| FuelLevelEmissionPerm | Double
| DieselEngineType | Text | Cummins | Cummins
| Governor | Text | PID | PID
| GobernorBrand | Text
| RatedPower_kVA_kW | Double | 200 | 200
| CompressionRatio_ | Text | 15:01 | 15:01
| NoofCylinder | Short Integer | 6 | 6
| Speed_RPM | Double | 1500 | 1500
| Applicable_Standard | Text
| SpeedREgulation | Short Integer
| Fuel_Tank_Capacity | Double | 500 | 500
| Cooling_System | Short Integer | Liquid -cooled closed loup | Liquid -cooled closed loup
| NoiseatFullLoad | Double | 97 | 97
| LubricationOilConsumption | Double | 0.025 | 0.025
| Ambient_temperature | Double
| Protection index | Text
| MethodofStarting | Text | Man/Auto | Man/Auto
| Voltage_VDC | Double | 24 | 24
| Power_kW | Double | 200 | 200
| Battery_Capacity_Ah | Double | 135 | 135
| BatteryType | Text | Lead-acid | Lead-acid
| BrandandModelofBattery | Text
| Frequency_Hz | Short Integer | 50 | 50
| VoltageRegulationMode | Short Integer
| Total_Weight | Double | 1453 | 1453

## SUBSTATION SHEET
GISAGARA
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | 10 | 10
| Substation_ID | Text | GSGR-039 | GSGR-039
| Substation_Total_Capacity_MVA | Double | 20MVA | 20
| Substation_Voltage_Level_kV | Short Integer | 220/30kV | 13
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 1 | 1
| Numbe_of_Earthing_Transfomer | Short Integer | 1 | 1
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | YES | 1
| Busbar_Configuration_HV | Short Integer | Single busbar | 1
| Number of MV Feeders | Short Integer | 6 | 6
| Number of HV line Bays | Short Integer | 2 | 2
| Number of Trx Bays | Short Integer | 1 | 1
| Configuration_Busbar_MV | Short Integer | Double busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2008 | 2020
| Year_of_upgrade | Short Integer | NA | 0
| Contractor_Name | Text | NCC | NCC
| Substation_Meter_SN | Text | NA | Not Existing
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1