## JABANA 2 SUBSTATION
JABANA 2
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-003 | PTR-1-003
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | JBNA-003 | JBNA-003
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | BEST | BEST
| CountryOfManufacturer | Text | TURKY | TURKY
| ManufacturerYear | Short Integer | 2008 | 2008
| Year_commissioning | Short Integer | 2008 | 2008
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 110/6.6kV | 7
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 15MVA | 15
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 6.6kV | 6.6
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 78.7A | 78.7
| SecondaryCurrent_A | Double | 1312A | 1312
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3Phase | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 12.11% | 12.11
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 15kW | 15
| LoadLosses | Double | 60kW | 60
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | CM-III-350-Y-72.5/B-14271G | CM-III-350-Y-72.5/B-14271G
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | SHANGAI HUAMING POWER EQUIPMENT | SHANGAI HUAMING POWER EQUIPMENT
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2008 | 2008
| SerialNumber | Text | M071457 | M071457
| Barcode | Text | NA | NA
| TotalWeight | Double | 33200kg | 33200
| WeightOfActivePart | Double | 17700kg | 17700
| WeightOfOil | Double | 9000kg | 9000
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | 25000kg | 25000
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-2-003 | PTR-2-003
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | JBNA-003 | JBNA-003
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 1
| Manufacturer | Text | BEST | BEST
| CountryOfManufacturer | Text | TURKY | TURKY
| ManufacturerYear | Short Integer | 2008 | 2008
| Year_commissioning | Short Integer | 2008 | 2008
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 110/6.6kV | 7
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 15MVA | 15
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 6.6kV | 6.6
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 78.7A | 78.7
| SecondaryCurrent_A | Double | 1312A | 1312
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 Phase | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 12.11% | 12.11
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 15kW | 15
| LoadLosses | Double | 60kW | 60
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | CM-III-350-Y-72.5/B-14271G | CM-III-350-Y-72.5/B-14271G
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | SHANGAI HUAMING POWER EQUIPMENT | SHANGAI HUAMING POWER EQUIPMENT
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2008 | 2008
| SerialNumber | Text | M071458 | M071458
| Barcode | Text | NA | NA
| TotalWeight | Double | 33200kg | 33200
| WeightOfActivePart | Double | 17700kg | 17700
| WeightOfOil | Double | 9000kg | 9000
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | 25000kg | 25000
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | Located inside the Power Plant | Located inside the Power Plant
| PowerPlantID | Text | Located inside the Power Plant | Located inside the Power Plant
| Substation_ID | Text | Located inside the Power Plant | Located inside the Power Plant
| PowerPlantname | Text | Located inside the Power Plant | Located inside the Power Plant
| TransformerNaming | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Manufacturer | Text | Located inside the Power Plant | Located inside the Power Plant
| CountryOfManufacturer | Text | Located inside the Power Plant | Located inside the Power Plant
| ManufacturerYear | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Owner | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Primaryvoltage__kv | Double | Located inside the Power Plant | Located inside the Power Plant
| Secondaryvoltage__kv | Double | Located inside the Power Plant | Located inside the Power Plant
| TertiaryCurrent_A | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Nominal_Frequency | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| PrimaryCurrent_A | Double | Located inside the Power Plant | Located inside the Power Plant
| SecondaryCurrent_A | Double | Located inside the Power Plant | Located inside the Power Plant
| TertiaryCurrent_A | Double | Located inside the Power Plant | Located inside the Power Plant
| Vector_Group_Trx | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| CoolingMethod | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Phases | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| WorkingCondition | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| PercentageImpedance | Double | Located inside the Power Plant | Located inside the Power Plant
| No_Load_losses | Double | Located inside the Power Plant | Located inside the Power Plant
| LoadLosses | Double | Located inside the Power Plant | Located inside the Power Plant
| AltitudeLevel | Double | Located inside the Power Plant | Located inside the Power Plant
| Noiselevel_db | Double | Located inside the Power Plant | Located inside the Power Plant
| NumberOfTappingPosition | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Standard_Code | Text | Located inside the Power Plant | Located inside the Power Plant
| Tap_changer | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| VoltageVariationRange1 | text | Located inside the Power Plant | Located inside the Power Plant
| Tap_changer_manufacturer | Text | Located inside the Power Plant | Located inside the Power Plant
| Tap_changer_country_orgin_ | Text | Located inside the Power Plant | Located inside the Power Plant
| TapChangerManufacturingDate | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| SerialNumber | Text | Located inside the Power Plant | Located inside the Power Plant
| Barcode | Text | Located inside the Power Plant | Located inside the Power Plant
| TotalWeight | Double | Located inside the Power Plant | Located inside the Power Plant
| WeightOfActivePart | Double | Located inside the Power Plant | Located inside the Power Plant
| WeightOfOil | Double | Located inside the Power Plant | Located inside the Power Plant
| WeightOfUpperTank | Double | Located inside the Power Plant | Located inside the Power Plant
| TransportationOfWeight_N2 | Double | Located inside the Power Plant | Located inside the Power Plant
| WeightOfAccessories | Double | Located inside the Power Plant | Located inside the Power Plant
| LV_CB_A | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Earthing_Switch | Short Integer | Located inside the Power Plant | Located inside the Power Plant
| Notes | Text | Located inside the Power Plant | Located inside the Power Plant
| Branch | text | Located inside the Power Plant | Located inside the Power Plant
| Year_commissioning | Short Integer | Located inside the Power Plant | Located inside the Power Plant
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | JBNA-002 | JBNA-002
| Busbar_HV_ID | Text | BB-003 | BB-003
| Number_of_Busbar_HV | Short Integer | 1 | 1
| Number_of_Busbar_MV | Short Integer | 1 | 1
| Type_of_Busbar | Short Integer | Tubular | Tubular
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | Aluminium | 1
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 110kV | 110
| Short_circuit_current_kA | Double | 50kA | 50
| Nominal_Current_A | Double | 960A | 960
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-001 | SWG-001
| Substation_ID | Text | JBNA-003 | JBNA-003
| FeederID | Text | J01 | J01
| FeederName | Text | STATION TRANSFORMER | STATION TRANSFORMER
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB only | 2
| Type_of_MV_cable_termination | Short Integer | Heat Shrinkable | 3
| Insulation_Medium | Short Integer | Air insulated | 3
| Manufacturing_Year | Short Integer | 2007 | 2007
| Serial_Number | Text | 1VLS1000015482/177082 | 1VLS1000015482/177082
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2007 | 2007
| Country_origin | Text | NORWAY | NORWAY
| Type_Model | Text | UNI GEAR | UNI GEAR
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 6.6KV | 6.6
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 6.6kV | 6.6
| Maximum_continu_system_voltage | Double | 12kV | 12
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 31.5kA | 31.5
| Ratedpeak_shortcircuitcurrent | Double | 80kA | 80
| RatedBusbar_Current | Double | 2000A | 2000
| Rated_SF6_Pressure_Kpa | Double | NA | NA
| Minimum_functional_level_for_SF6__KPa_ | Double | NA | NA
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001 | SWG-001
| Substation_ID | Text | JBNA-003 | JBNA-003
| FeederID | Text | J02 | J02
| FeederName | Text | INCOMER TR1 | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB only | 2
| Type_of_MV_cable_termination | Short Integer | Heat Shrinkable | 3
| Insulation_Medium | Short Integer | Air insulated | 3
| Manufacturing_Year | Short Integer | 2007 | 2007
| Serial_Number | Text | 1VLS1000015482/177083 | 1VLS1000015482/177083
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2007 | 2007
| Country_origin | Text | NORWAY | NORWAY
| Type_Model | Text | UNI GEAR | UNI GEAR
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 6.6KV | 6.6
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 6.6kV | 6.6
| Maximum_continu_system_voltage | Double | 12kV | 12
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 31.5kA | 31.5
| Ratedpeak_shortcircuitcurrent | Double | 80kA | 80
| RatedBusbar_Current | Double | 2000A | 2000
| Rated_SF6_Pressure_Kpa | Double | NA | NA
| Minimum_functional_level_for_SF6__KPa_ | Double | NA | NA
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001 | SWG-001
| Substation_ID | Text | JBNA-003 | JBNA-003
| FeederID | Text | J03 | J03
| FeederName | Text | INCOMER TR2 | INCOMER TR2
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB only | 2
| Type_of_MV_cable_termination | Short Integer | Heat Shrinkable | 3
| Insulation_Medium | Short Integer | Air insulated | 3
| Manufacturing_Year | Short Integer | 2007 | 2007
| Serial_Number | Text | 1VLS1000015482/177084 | 1VLS1000015482/177084
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2007 | 2007
| Country_origin | Text | NORWAY | NORWAY
| Type_Model | Text | UNI GEAR | UNI GEAR
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 6.6KV | 6.6
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 6.6kV | 6.6
| Maximum_continu_system_voltage | Double | 12kV | 12
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 31.5kA | 31.5
| Ratedpeak_shortcircuitcurrent | Double | 80kA | 80
| RatedBusbar_Current | Double | 2000A | 2000
| Rated_SF6_Pressure_Kpa | Double | NA | NA
| Minimum_functional_level_for_SF6__KPa_ | Double | NA | NA
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001 | SWG-001
| Substation_ID | Text | JBNA-003 | JBNA-003
| FeederID | Text | J04 | J04
| FeederName | Text | INCOMER G1 | INCOMER G1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB only | 2
| Type_of_MV_cable_termination | Short Integer | Heat Shrinkable | 3
| Insulation_Medium | Short Integer | Air insulated | 3
| Manufacturing_Year | Short Integer | 2007 | 2007
| Serial_Number | Text | 1VLS1000015482/177085 | 1VLS1000015482/177085
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2007 | 2007
| Country_origin | Text | NORWAY | NORWAY
| Type_Model | Text | UNI GEAR | UNI GEAR
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 6.6KV | 6.6
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 6.6kV | 6.6
| Maximum_continu_system_voltage | Double | 12kV | 12
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 31.5kA | 31.5
| Ratedpeak_shortcircuitcurrent | Double | 80kA | 80
| RatedBusbar_Current | Double | 2000A | 2000
| Rated_SF6_Pressure_Kpa | Double | NA | NA
| Minimum_functional_level_for_SF6__KPa_ | Double | NA | NA
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001 | SWG-001
| Substation_ID | Text | JBNA-003 | JBNA-003
| FeederID | Text | J05 | J05
| FeederName | Text | INCOMER G2 | INCOMER G2
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB only | 2
| Type_of_MV_cable_termination | Short Integer | Heat Shrinkable | 3
| Insulation_Medium | Short Integer | Air insulated | 3
| Manufacturing_Year | Short Integer | 2007 | 2007
| Serial_Number | Text | 1VLS1000015482/177086 | 1VLS1000015482/177086
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2007 | 2007
| Country_origin | Text | NORWAY | NORWAY
| Type_Model | Text | UNI GEAR | UNI GEAR
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 6.6KV | 6.6
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 6.6kV | 6.6
| Maximum_continu_system_voltage | Double | 12kV | 12
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 31.5kA | 31.5
| Ratedpeak_shortcircuitcurrent | Double | 80kA | 80
| RatedBusbar_Current | Double | 2000A | 2000
| Rated_SF6_Pressure_Kpa | Double | NA | NA
| Minimum_functional_level_for_SF6__KPa_ | Double | NA | NA
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001 | SWG-001
| Substation_ID | Text | JBNA-003 | JBNA-003
| FeederID | Text | J06 | J06
| FeederName | Text | MEASUREMENT | MEASUREMENT
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | Isolator only | 3
| Type_of_MV_cable_termination | Short Integer | NA | 3
| Insulation_Medium | Short Integer | Air insulated | 3
| Manufacturing_Year | Short Integer | 2007 | 2007
| Serial_Number | Text | 1VLS1000015482/177087 | 1VLS1000015482/177087
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2007 | 2007
| Country_origin | Text | NORWAY | NORWAY
| Type_Model | Text | UNI GEAR | UNI GEAR
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 6.6KV | 6.6
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 6.6kV | 6.6
| Maximum_continu_system_voltage | Double | 12kV | 12
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 31.5kA | 31.5
| Ratedpeak_shortcircuitcurrent | Double | 80kA | 80
| RatedBusbar_Current | Double | 2000A | 2000
| Rated_SF6_Pressure_Kpa | Double | NA | NA
| Minimum_functional_level_for_SF6__KPa_ | Double | NA | NA
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | E01 | E01
| Substation_ID | Text | JBNA-003 | JBNA-003
| Line_Bay_Name | Text | JABANA 1 | JABANA 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 542plus | ABB-REF 542plus
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1 | VT2-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2 | VT2-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3 | VT2-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1 | VT3-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2 | VT3-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3 | VT3-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-1 | VT4-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ELECTROPUTER | ELECTROPUTER
| CountryOfManufacturer | Text | ROMANIA | ROMANIA
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 123kV | 123
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-2 | VT4-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ELECTROPUTER | ELECTROPUTER
| CountryOfManufacturer | Text | ROMANIA | ROMANIA
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 123kV | 123
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-3 | VT4-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ELECTROPUTER | ELECTROPUTER
| CountryOfManufacturer | Text | ROMANIA | ROMANIA
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 60044-1 | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 123kV | 123
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772012 | 1HSE8772012
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772013 | 1HSE8772013
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772014 | 1HSE8772014
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT2-1 | CT2-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772015 | 1HSE8772014
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT2-2 | CT2-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772016 | 1HSE8772016
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT2-3 | CT2-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772017 | 1HSE8772017
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772018 | 1HSE8772018
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | Oil, Others
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772019 | 1HSE8772019
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | Oil, Others
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2008 | 2008
| Standard_Code | Text | IEC60044-1 | IEC60044-1
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 120-240A | 240
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8772021 | 1HSE8772021
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | Oil, Others
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | AREVA T&D | AREVA T&D
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 7386-10-2032913/2 | 7386-10-2032913/2
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1424kg | 1424
| TotalMassofInsulatingMed | Double | 9.9kg | 9.9
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | SIEYUAN | SIEYUAN
| CircuitBreakerID | Text | CB2 | CB2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2023 | 2023
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | DH230617 | DH230617
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.6 Mpa | 0.6
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1700kg | 1700
| TotalMassofInsulatingMed | Double | 8kg | 8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | SIEYUAN | SIEYUAN
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2023 | 2023
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | DH230618 | DH230618
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.6 Mpa | 0.6
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1700kg | 1700
| TotalMassofInsulatingMed | Double | 8kg | 8
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1 | Q1-1
| Substation | Text | JBNA-003 | JBNA-003
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | SIEMENS | SIEMENS
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | JBNA-003 | JBNA-003
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | SIEMENS | SIEMENS
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Short Integer | 2008 | 2008
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2 | Q1-2
| Substation | Text | JBNA-003 | JBNA-003
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | AREVA T&D | AREVA T&D
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2009 | 2009
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 11
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3 | Q1-3
| Substation | Text | JBNA-003 | JBNA-003
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | AREVA T&D | AREVA T&D
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2009 | 2009
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | JABANA 2 | 58
| Substation_ID | Text | JBNA-003 | JBNA-003
| Substation_Total_Capacity_MVA | Double | 30MVA | 30
| Substation_Voltage_Level_kV | Short Integer | 110/6.6kV | 3
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 2 | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 0 | 0
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | Located in Power Plant | Located in Power Plant
| Standby_Generators | Short Integer | Yes | 1
| Busbar_Configuration_HV | Short Integer | Single busbar | Single busbar
| Number of MV Feeders | Short Integer | 6 | 6
| Number of HV line Bays | Short Integer | 1 | 1
| Number of Trx Bays | Short Integer | 2 | 2
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | Air Insulated | 2
| Year of Commissioning | Short Integer | 2009 | 2009
| Year_of_upgrade | Short Integer | Not yet upgraded | Not yet upgraded
| Contractor_Name | Text | WARTSILA | WARTSILA
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | No | 0
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1200 | NPT1200
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | MKGW-025 | MKGW-025
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES, | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-1 | SA2-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-2 | SA2-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-3 | SA2-3
| Substation_ID | Text | JBNA-002 | JBNA-002
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-1 | SA3-1
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-2 | SA3-2
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | EGYTRAFO | EGYTRAFO
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | EGYPTE | EGYPTE
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947 | IEC 60439/60947
| BatteryFloatingVoltage | Double | 50V | 50
| RatedVoltage | Double | 48V | 48
| TenHrsRatingCapacity | Double | 60Ah | 60
| One_min_rating_Current_A | Double | 180A | 180
| MaximumVolatge_V | Double | 68V | 68
| MinimumVoltage_V | Double | 40V | 40
| MinimumVoltageperCell | Double | 1.2V | 1.2
| NumberofCells | Short Integer | 40 | 40
| BatteryFloatingVoltage | Double | 50 | 50
| BoostChargingVoltage | Double | 56V | 56V
| FloatChargeCurrent_A | Double | 6.2A | 6.2A
| BoostChargeCurrent | Double | 75A | 75A
| SelfDischargeat_25oC | Double | 7% | 7
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 5hrs | 5
DC Supply 110 VDC Battery | Manufacturer | Text | EGYTRAFO | EGYTRAFO
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | EGYPTE | EGYPTE
| Model | Text | KMP 250 P | KMP 250 P
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110V | 110
| TenHrsRatingCapacity | Double | 250Ah | 250
| One_min_rating_Current_A | Double | 100A | 100
| MaximumVolatge_V | Double | 126.5V | 126.5
| MinimumVoltage_V | Double | 93.5V | 93.5
| MinimumVoltageperCell | Double | 2 | 2
| Number_of_cells__No_ | Long Integer | 56 | 56
| BatteryFloatingVoltage | Double | 112.5V | 112.5
| BoostChargingVoltage | Double | 132.3V | 132.3
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 100A | 100
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | AEG GmbH | AEG GmbH
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Model | Text | Profitec 2000 S 48V/60A | Profitec 2000 S 48V/60A
| Charger_type | Short Integer | Thyristor controlled | 1
| Standards_ | Short Integer | DIN41773 | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 5.53kVA | 5.53
| DC Output (Kw) | Double | 2.88kW | 2.88
| DC_Output_kV | Double | 48V | 48
| Rated_output_Voltage_V | Double | 48V | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000m | 2000
| Degree_protection_ | Short Integer | IP 20 | IP 20
| DCDistributionBoard | Short Integer | No | No
| RatedCurrent_A | Double | NA | NA
| NumberofFeeders | Short Integer | NA | NA
| short_circuit_capacity_breaker | Double | NA | NA
DC Supply 110 VDC charger | Manufacturer | Text | EDITELEKITRONIK | EDITELEKITRONIK
| Substation_ID | Text | JBNA-003 | JBNA-003
| CountryOfManufacturer | Text | TURKY | TURKY
| Model | Text | ERD-3P/110/100A | ERD-3P/110/100A
| TypeofOperation | Short Integer | Parallel | 2
| Charger_type | Short Integer | THYROTRONIC | 2
| Standards_ | Text | IEC 61000-6-4 | IEC 61000-6-4
| ChargingTime | Double | 5h | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 20kVA | 20
| VoltageVariation | Double | ±5% | ±5%
| DC_Output_kV | Double | 110V | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110V | 110
| MaximumDC_Voltage_V | Double | 126V | 126
| ConstantVoltageAccuracy | Double | ±10% | ±10%
| Rated_DC_output_Current_A | Double | 100A | 100
| FloatingVoltageRegulatin | Double | 104.4V | 104.4
| EqualisingVoltageRegulatin | Double | 128.8V | 128.8
| Minimum_Insulation_resistance_ | Double | 5MΏ
| TypeofCooling | Short Integer | Natural self-ventilating, Others | 1
| Ambient_temperature | Double | 0°C to +40°C | 0°C to +40°C
| Altitude_m | Double | >1000m | 1000
| Total_Weight_Charger_kg | Double | 340kg | 340
| Degree_protection_ | Short Integer | IP20 | IP20
| RatedCurrent_A | Double | 100A | 100
| ShortCircuitStrength_kA_sec | Double | Not provided | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate, Others | Copper tin-plate,
DIGITAL fault recorder | Manufacturer | Text | Not Existing
| Country_Manufacture | Text | Not Existing
| Type | Text | Not Existing
| Standards | Text | Not Existing
| Arrangement | Short Integer | Not Existing
| VT_CT_Connection | Short Integer | Not Existing
| Frequency_Hz | Short Integer | Not Existing
| Nominal_input_current_A | Double | Not Existing
| Nominal_voltage_Vdc | Double | Not Existing
| Power_consumption_VA | Double | Not Existing
| NumberofAnalogInputs | Short Integer | Not Existing
| NumberofBinaryInputs | Short Integer | Not Existing
| NumberofBinaryOutputs | Short Integer | Not Existing
| Surge_withstand_capability_KV_ | Double | Not Existing
| Operating_temperature_oC | Double | Not Existing
High Voltage Line | Name | Text | JABANA 1 | JABANA 1
| Year_of_commisioning | Short Integer | 2009 | 2009
| ContractorName | Text | SAG | SAG
| Manufacturer | Text | 1972 | 1972
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR,CU | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 1.3km | 1.3
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 130kN | 130
| MaxElectricResitance | Double | 0.119(Ώ/km) | 0.119
| PositiveSequenceReactance | Double | 0.427(Ω/km) | 0.427
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119
| ZeroSequenceCapacitance | Double | 0.011(µf/km) | 0.011
| PositiveSequenceCapacitance | Double | 0.0066(µF/km) | 0.0066
Transformer Bay | Trx_Bay_ID | Text | E02 | E02
| Substation_ID | Text | JBNA-003 | JBNA-003
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 15MVA | 15
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | ABB-RET630 | ABB-RET630
| Type_of_Back_up_relay | Text | VAMP 50 | VAMP 50
| Type_of_BCU_Bay_control_unit | Text | ABB - REF542+ | ABB - REF542+
Transformer Bay | Trx_Bay_ID | Text | E03 | E03
| Substation_ID | Text | JBNA-003 | JBNA-003
| Trx_Bay_Name | Text | TRANSFORMER 2 | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 15MVA | 15
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | ABB-RET630 | ABB-RET630
| Type_of_Back_up_relay | Text | VAMP 50 | VAMP 50
| Type_of_BCU_Bay_control_unit | Text | ABB - REF542+ | ABB - REF542+
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | NORWAY | NORWAY
| Type__model | Text | VD4G40 | VD4G40
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 6.6kV | 6.6
| MaxContinuousOperatVolt_kV | Double | 12kV | 12
| RatedImpulseWithstandVol | Double | 95kV | 95
| PowerFrequencyWithstandVol | Double | 38kV | 38
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| RatedNormalCurrent_A | Double | 2000A | 2000
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | Data collection require shutdown
| CurrentTransfomer_ID | Text | Data collection require shutdown
Data collection require shutdown
| CountryOfManufacturer | Text | Data collection require shutdown
| Type__model | Text | Data collection require shutdown
| Standard | Text | Data collection require shutdown
| RatedVoltage_kV1 | Double | Data collection require shutdown
| Rated_Frequency | Short Integer | Data collection require shutdown
| Number_phases | Long Integer | Data collection require shutdown
| NumberofCores | Short Integer | Data collection require shutdown
| Rated_Primary_Current_A | Double | Data collection require shutdown
| Rated_Secondary_Current | Double | Data collection require shutdown
| AccuracyClass | Text | Data collection require shutdown
| Burden_VA | Double | Data collection require shutdown
| RatedShortTimeWithstandCur | Double | Data collection require shutdown
| Rated_Peak_Short_Cir_Current | Double | Data collection require shutdown
| RatedImpulseWithstandVol | Double | Data collection require shutdown
| LimitsContPrimaryCurrency_A | Double | Data collection require shutdown
Indoor Voltage Transformer | Manufacturer | Text | Data collection require shutdown
| VoltageTransfomer_ID | Text | Data collection require shutdown
Data collection require shutdown
| CountryOfManufacturer | Text | Data collection require shutdown
| Standard | Text | Data collection require shutdown
| TypeofVoltageTransformer | Short Integer | Data collection require shutdown
| Rated_Frequency | Short Integer | Data collection require shutdown
| Number_phases | Long Integer | Data collection require shutdown
| PowerFrequencyWithstandVol | Double | Data collection require shutdown
| RatedImpulseWithstandVol | Double | Data collection require shutdown
| RatedPrimaryVoltage_kV | Double | Data collection require shutdown
| Rated_secondary_voltage_winding_1__V_ | Text | Data collection require shutdown
| Rated_secondary_voltage_winding_2__V_ | Text | Data collection require shutdown
| Accuracy_class__measuring_ | Text | Data collection require shutdown
| Accuracy_class__protection_ | Text | Data collection require shutdown
| RatedOutput_VA | Double | Data collection require shutdown
| TertiaryVoltage_kV | Long Integer | Data collection require shutdown
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-002 | TSP-CPR-1-002
| Substation_ID | Text | JBNA-003 | JBNA-003
| Bay_ID | Text | E01 | E01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1-5A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | ABB-RET 630 | ABB-RET 630
| Bay_ID | Text | E04 | E04
| Substatoin_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| Country_manufacturer_ | Text | NORWAY | NORWAY
| SecondaryCurrent_A | Short Integer | 1-5A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | ABB-RET 630 | ABB-RET 630
| Bay_ID | Text | E04 | E04
| Substatoin_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | ABB | ABB
| Country_manufacturer_ | Text | NORWAY | NORWAY
| SecondaryCurrent_A | Short Integer | 1-5A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | JBNA-003 | JBNA-003
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Included in Power Plant | Included in Power Plant
| Substation_ID | Text | Included in Power Plant | Included in Power Plant
| Standby_Generator_ID | Text | Included in Power Plant | Included in Power Plant
| CountryOfManufacturer | Text | Included in Power Plant | Included in Power Plant
| Mode_Operation | Short Integer | Included in Power Plant | Included in Power Plant
| Model | Text | Included in Power Plant | Included in Power Plant
| Type_Assembly | Short Integer | Included in Power Plant | Included in Power Plant
| Arrangement | Short Integer | Included in Power Plant | Included in Power Plant
| Phases | Short Integer | Included in Power Plant | Included in Power Plant
| RatedOuptuPower_kVA | Double | Included in Power Plant | Included in Power Plant
| RatedVoltage | Double | Included in Power Plant | Included in Power Plant
| RatedCurrent_A | Double | Included in Power Plant | Included in Power Plant
| PowerFactor | Double | Included in Power Plant | Included in Power Plant
| CouplingofEngine | Text | Included in Power Plant | Included in Power Plant
| FuelLevelEmissionPerm | Double | Included in Power Plant | Included in Power Plant
| DieselEngineType | Text | Included in Power Plant | Included in Power Plant
| Governor | Text | Included in Power Plant | Included in Power Plant
| GobernorBrand | Text | Included in Power Plant | Included in Power Plant
| RatedPower_kVA_kW | Double | Included in Power Plant | Included in Power Plant
| CompressionRatio_ | Text | Included in Power Plant | Included in Power Plant
| NoofCylinder | Short Integer | Included in Power Plant | Included in Power Plant
| Speed_RPM | Double | Included in Power Plant | Included in Power Plant
| Applicable_Standard | Text | Included in Power Plant | Included in Power Plant
| SpeedREgulation | Short Integer | Included in Power Plant | Included in Power Plant
| Fuel_Tank_Capacity | Double | Included in Power Plant | Included in Power Plant
| Cooling_System | Short Integer | Included in Power Plant | Included in Power Plant
| NoiseatFullLoad | Double | Included in Power Plant | Included in Power Plant
| LubricationOilConsumption | Double | Included in Power Plant | Included in Power Plant
| Ambient_temperature | Double | Included in Power Plant | Included in Power Plant
| Protection index | Text | Included in Power Plant | Included in Power Plant
| MethodofStarting | Text | Included in Power Plant | Included in Power Plant
| Voltage_VDC | Double | Included in Power Plant | Included in Power Plant
| Power_kW | Double | Included in Power Plant | Included in Power Plant
| Battery_Capacity_Ah | Double | Included in Power Plant | Included in Power Plant
| BatteryType | Text | Included in Power Plant | Included in Power Plant
| BrandandModelofBattery | Text | Included in Power Plant | Included in Power Plant
| Frequency_Hz | Short Integer | Included in Power Plant | Included in Power Plant
| VoltageRegulationMode | Short Integer | Included in Power Plant | Included in Power Plant
| Total_Weight | Double | Included in Power Plant | Included in Power Plant

## Sheet1
JABANA 2
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | JABANA 2 | 58
| Substation_ID | Text | JBNA-003 | JBNA-004
| Substation_Total_Capacity_MVA | Double | 30MVA | 30
| Substation_Voltage_Level_kV | Short Integer | 110/6.6kV | 3
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 2 | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 0 | 0
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | Located in Power Plant | Located in Power Plant
| Standby_Generators | Short Integer | Yes | 1
| Busbar_Configuration_HV | Short Integer | Single busbar | 1
| Number of MV Feeders | Short Integer | 6 | 6
| Number of HV line Bays | Short Integer | 1 | 1
| Number of Trx Bays | Short Integer | 2 | 2
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | Air Insulated | 2
| Year of Commissioning | Short Integer | 2009 | 2009
| Year_of_upgrade | Short Integer | NA | 0
| Contractor_Name | Text | WARTSILA | WARTSILA
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | No | 0