## MONT KIGALI 1 SUBSTATION
BUGARAMA
Device | Field | Data Type | Domain | Domain Code
Power Transformer | transfomerID | Text | PTR-1-004 | PTR-1-004
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | MKGL-004 | MKGL-004
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | ETRA | ETRA
| CountryOfManufacturer | Text | SLOVENIA | SLOVENIA
| ManufacturerYear | Short Integer | 2017 | 2017
| Year_commissioning | Short Integer | 2017 | 2017
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 110/30kV | 4
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 20MVA | 20
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 30kV | 30
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 105A | 105
| SecondaryCurrent_A | Double | 385A | 385
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 8.25% | 8.25
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 22.53kW | 22.53
| LoadLosses | Double | 90kW | 90
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | MIII3504-170/B-142716 | MIII3504-170/B-142716
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2017 | 2017
| SerialNumber | Text | 1822457 | 1822457
| Barcode | Text | NA | NA
| TotalWeight | Double | 44000kg | 44000
| WeightOfActivePart | Double | 13650kg | 13650
| WeightOfOil | Double | 111000kg | 111000
| WeightOfUpperTank | Double | 22500kg | 22500
| TransportationOfWeight_N2 | Double | 36000kg | 36000
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer | transfomerID | Text | PTR-2-004 | PTR-2-004
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | MKGL-004 | MKGL-004
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | ETRA | ETRA
| CountryOfManufacturer | Text | SLOVENIA | SLOVENIA
| ManufacturerYear | Short Integer | 2017 | 2017
| Year_commissioning | Short Integer | 2017 | 2017
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 110/15kV | 5
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 20MVA | 20
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 15kV | 15
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 107.7A | 107.7
| SecondaryCurrent_A | Double | 769.8A | 769.8
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNyn0+d11 | 17
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 11% | 11
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 11kW | 11
| LoadLosses | Double | 59.97kW | 59.97
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | MIII3504-170/B-14273G | MIII3504-170/B-14273G
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2017 | 2017
| SerialNumber | Text | 1363170 | 1363170
| Barcode | Text | NA | NA
| TotalWeight | Double | 44000kg | 44000
| WeightOfActivePart | Double | 12300kg | 12300
| WeightOfOil | Double | 10800kg | 10800
| WeightOfUpperTank | Double | 22500kg | 22500
| TransportationOfWeight_N2 | Double | 36500kg | 36500
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | ETR-1-004 | ETR-1-004
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | MKGL-004 | MKGL-004
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | TR1
| Manufacturer | Text | TRAFO ELETTRO | TRAFO ELETTRO
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2019 | 2019
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 30/0.4kV | 1
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 0.160MVA | 0.16
| Primaryvoltage__kv | Double | 30kV | 30
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | Not Exising | Not Exising
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 3.08A | 3.08
| SecondaryCurrent_A | Double | 230.95A | 230.95
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | Zyn11 | 12
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | Outdoor | 2
| PercentageImpedance | Double | 2.8% | 3
| No_Load_losses | Double | 2kW | 2
| LoadLosses | Double | 0.5KW | 0.5
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 3 | 3
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | OFF LOAD | OFF LOAD
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | TRAFO ELETTRO | TRAFO ELETTRO
| Tap_changer_country_orgin_ | Text | ITALY | ITALY
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 4640kg | 4640
| WeightOfActivePart | Double | 2100kg | 2100
| WeightOfOil | Double | 1320kg | 1320
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 250A | 250
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2019 | 2019
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | MKGL-004 | MKGL-004
| Busbar_HV_ID | Text | BB-004 | BB-004
| Number_of_Busbar_HV | Short Integer | 1 | 1
| Number_of_Busbar_MV | Short Integer | 1 | 1
| Type_of_Busbar | Short Integer | Tubular | Tubular
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | Aluminium | 1
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 110kV | 110
| Short_circuit_current_kA | Double | 50kA | 50
| Nominal_Current_A | Double | 960A | 960
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | H01 | H01
| FeederName | Text | INCOMER TR1 | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV916714-000050/001 | CV916714-000050/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | H02 | H02
| FeederName | Text | KANAZI | KANAZI
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV916714-000060/001 | CV916714-000060/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50k
| Smart_meter_Installed | Short Integer | Yes | 1
| Meter_number___if_yes_ | Text | MLHJ3000730 | MLHJ3000730
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | H03 | H03
| FeederName | Text | KIYUMBA | KIYUMBA
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV916714-000070/001 | CV916714-000070/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70k
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | Yes | 1
| Meter_number___if_yes_ | Text | MLH2000049 | MLH2000049
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | H04 | H04
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV916714-000080/001 | CV916714-000080/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | H05 | H05
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | SF6
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV916714-000090/001 | CV916714-000090/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | K01 | K01
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV91469-000050/001 | CV91469-000050/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 15KV | 15
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 24kV | 24
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | K02 | K02
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV91469-000060/001 | CV91469-000060/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 15KV | 15
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 24kV | 24
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | K03 | K03
| FeederName | Text | GIKONDO | GIKONDO
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV91469-000070/001 | CV91469-000070/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 15KV | 15
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 24kV | 24
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | Yes | 1
| Meter_number___if_yes_ | Text | HLJ3000732 | HLJ3000732
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | K04 | K04
| FeederName | Text | NYARURAMA | NYARURAMA
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV91469-000080/001 | CV91469-000080/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 15KV | 15KV
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 24kV | 24
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | Yes | 1
| Meter_number___if_yes_ | Text | HLJ3000731 | HLJ3000731
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | K05 | K05
| FeederName | Text | NYAMIRAMBO | NYAMIRAMBO
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV91469-000090/001 | CV91469-000090/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 15KV | 15
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 24kV | 24
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | Yes | 1
| Meter_number___if_yes_ | Text | HLQA00027 | HLQA00027
MV Switch gear | SwitchGearID | Text | SWG-004 | SWG-004
| Substation_ID | Text | MKGL-004 | MKGL-004
| FeederID | Text | K06 | K06
| FeederName | Text | INCOMER TR1 | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV91469-0000100/001 | CV91469-0000100/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 15KV | 15
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 24kV | 24
| type_protection_relay | Short Integer | REF 630 | REF 630
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 70kPa | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa | 50
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | E01 | E01
| Substation_ID | Text | MKGL-004 | MKGL-004
| Line_Bay_Name | Text | KIGOMA | KIGOMA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 630 | ABB-REF 630
Line Bay | Line_Bay_ID | Text | E02 | E02
| Substation_ID | Text | MKGL-004 | MKGL-004
| Line_Bay_Name | Text | GAHANGA | GAHANGA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 630 | ABB-REF 630
Line Bay | Line_Bay_ID | Text | E03 | E03
| Substation_ID | Text | MKGL-004 | MKGL-004
| Line_Bay_Name | Text | GIKONDO | GIKONDO
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 630 | ABB-REF 630
Line Bay | Line_Bay_ID | Text | E04 | E04
| Substation_ID | Text | MKGL-004 | MKGL-004
| Line_Bay_Name | Text | JABANA 1 | JABANA 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 110
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 630 | ABB-REF 630
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1 | VT2-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2 | VT2-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3 | VT2-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1 | VT3-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2 | VT3-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3 | VT3-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-1 | VT4-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-2 | VT4-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-3 | VT4-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-1 | VT5-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-2 | VT5-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-3 | VT5-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866007 | 1HSE8866007
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866021 | 1HSE8866021
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866030 | 1HSE8866030
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT2-1 | CT2-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866035 | 1HSE8866035
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT2-2 | CT2-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866019 | 1HSE8866019
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT2-3 | CT2-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866014 | 1HSE8866014
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866036 | 1HSE8866036
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866011 | 1HSE8866011
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866039 | 1HSE8866039
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT4-1 | CT4-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866013 | 1HSE8866013
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT4-2 | CT4-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866027 | 1HSE8866027
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT4-3 | CT4-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Text | 2015 | 2015
| Standard_Code | Double | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Text | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Double | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Text | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Short Integer | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Double | 2 | 2
| Rated_Primary_Current_A | Short Integer | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Double | 1HSE8866022 | 1HSE8866022
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Text | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Double | Oil, Others | 1
| Degree_of_Protection | Short Integer | IP55 | IP55
| RatedContThermCurrentFactor_A | Text | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT5-1 | CT5-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866028 | 1HSE8866028
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT5-2 | CT5-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866010 | 1HSE8866010
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT5-3 | CT5-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866015 | 1HSE8866015
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT6-1 | CT6-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866028 | 1HSE8866028
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT6-2 | CT6-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866010 | 1HSE8866010
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT6-3 | CT6-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 40kA | 40
| Rated_Peak_Short_Cir_Current | Double | 100kA | 100
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1HSE8866015 | 1HSE8866015
| SF_ALF | Text | 5_20 | 20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV | 275
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712010 | 1HSB01712010
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000m
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1943kg | 1943
| TotalMassofInsulatingMed | Double | 11kg | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB2 | CB2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712013 | 1HSB01712013
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1943kg | 1943
| TotalMassofInsulatingMed | Double | 11kg | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSEB01712012 | 1HSEB01712012
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1943kg | 1943
| TotalMassofInsulatingMed | Double | 11kg | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB4 | CB4
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSEB01712011 | 1HSEB01712011
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1943kg | 1943
| TotalMassofInsulatingMed | Double | 11kg | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB5 | CB5
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712007 | 1HSB01712007
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1943kg | 1943
| TotalMassofInsulatingMed | Double | 11kg | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB6 | CB6
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712009 | 1HSB01712009
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1943kg | 1943
| TotalMassofInsulatingMed | Double | 11kg | 11
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1 | Q1-1
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2 | Q1-2
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2 | Q9-2
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3 | Q1-3
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-3 | Q9-3
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-4 | Q1-4
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-4 | Q9-4
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-5 | Q1-5
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-6 | Q1-6
| Substation | Text | MKGL-004 | MKGL-004
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | MONT KIGALI | 23
| Substation_ID | Text | MKGL-004 | MKGL-004
| Substation_Total_Capacity_MVA | Double | 40MVA | 40
| Substation_Voltage_Level_kV | Short Integer | 110/30/15kV | 13
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 2 | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 1 | 1
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | No | 0
| Busbar_Configuration_HV | Short Integer | Single busbar | 1
| Number of MV Feeders | Short Integer | 11 | 11
| Number of HV line Bays | Short Integer | 4 | 4
| Number of Trx Bays | Short Integer | 2 | 2
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Tubular | 2
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2017 | 2017
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | ELTEL | ELTEL
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 0
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1200 | NPT1200
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | MKGL-004 | MKGL-004
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES, | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-1 | SA2-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-2 | SA2-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA2-3 | SA2-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-1 | SA3-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-2 | SA3-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA4-1 | SA4-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA4-2 | SA4-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA4-3 | SA4-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA5-1 | SA5-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA5-2 | SA5-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA5-3 | SA5-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA6-1 | SA6-1
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA6-2 | SA6-2
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA6-3 | SA6-3
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| BatteryFloatingVoltage | Double | 50V | 50
| RatedVoltage | Double | 48V | 48
| TenHrsRatingCapacity | Double | 60Ah | 60
| One_min_rating_Current_A | Double | 120A | 120
| MaximumVolatge_V | Double | 48+15% | 55.2
| MinimumVoltage_V | Double | 48-15% | 40.8
| MinimumVoltageperCell | Double | 1.02V | 1.02
| NumberofCells | Short Integer | 38 | 38
| BatteryFloatingVoltage | Double | 53.9V | 53.9
| BoostChargingVoltage | Double | 55.8V | 55.8
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 60A | 60
| SelfDischargeat_25oC | Double | 7% | 7
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 5hrs | 5
DC Supply 110 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Model | Text | KL125P | KL125P
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110V | 110
| TenHrsRatingCapacity | Double | 125 Ah | 125
| One_min_rating_Current_A | Double | 100A | 100
| MaximumVolatge_V | Double | 110+15% | 126.5
| MinimumVoltage_V | Double | 110-15% | 93.5
| MinimumVoltageperCell | Double | 1.0V | 1
| Number_of_cells__No_ | Long Integer | 82 | 82
| BatteryFloatingVoltage | Double | 126V | 126
| BoostChargingVoltage | Double | 136.4V | 136.4
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 100A | 100
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | BENNING | BENNING
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | AUSTRIA | AUSTRIA
| Model | Text | D400G48.0/80 | D400G48.0/80
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN41773 | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 5.53kVA | 5.53
| DC Output (Kw) | Double | 2.88kW | 2.88
| DC_Output_kV | Double | 48V | 48
| Rated_output_Voltage_V | Double | 48V | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000m | 2000
| Degree_protection_ | Short Integer | IP 20 | IP 20
| DCDistributionBoard | Short Integer | No | No
| RatedCurrent_A | Double | NA | NA
| NumberofFeeders | Short Integer | NA | NA
| short_circuit_capacity_breaker | Double | NA | NA
DC Supply 110 VDC charger | Manufacturer | Text | BENNING | BENNING
| Substation_ID | Text | MKGL-004 | MKGL-004
| CountryOfManufacturer | Text | AUSTRIA | AUSTRIA
| Model | Text | D400G104.4/80 | D400G104.4/80
| TypeofOperation | Short Integer | Parallel | Parallel
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Text | DIN41773 | DIN41773
| ChargingTime | Double | 5h | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 14.8kVA | 14.8
| VoltageVariation | Double | ±5% | ±5%
| DC_Output_kV | Double | 110V | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110V | 110
| MaximumDC_Voltage_V | Double | 126V | 126
| ConstantVoltageAccuracy | Double | ±10% | ±10%
| Rated_DC_output_Current_A | Double | 100A | 100
| FloatingVoltageRegulatin | Double | 104.4V | 104.4
| EqualisingVoltageRegulatin | Double | 128.8V | 128.8
| Minimum_Insulation_resistance_ | Double | 5MΏ | 5
| TypeofCooling | Short Integer | Natural self-ventilating, Others | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C | 0°C to +40°C
| Altitude_m | Double | >1000m | 1000
| Total_Weight_Charger_kg | Double | 250kg | 250
| Degree_protection_ | Short Integer | IP20 | IP20
| RatedCurrent_A | Double | 100A | 100
| ShortCircuitStrength_kA_sec | Double | Not provided | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate | Copper tin-plate
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE | FRANCE
| Type | Text | REASON DR60 | REASON DR60
| Standards | Text | IEC61850 | IEC61850
| Arrangement | Short Integer | Panel mounted | Panel mounted
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A | 1
| Nominal_voltage_Vdc | Double | 110DC | 110
| Power_consumption_VA | Double | 150VA | 150
| NumberofAnalogInputs | Short Integer | 32 | 32
| NumberofBinaryInputs | Short Integer | 96 | 96
| NumberofBinaryOutputs | Short Integer | 48 | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | KIGOMA | KIGOMA
| Year_of_commisioning | Short Integer | 1974 | 1974
| ContractorName | Text | SGEEM | SGEEM
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 40.4km | 40.4
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 130kN | 130
| MaxElectricResitance | Double | 0.119(Ώ/km) | 0.119
| PositiveSequenceReactance | Double | 0.427(Ω/km) | 0.427
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119
| ZeroSequenceCapacitance | Double | 0.011(µf/km) | 0.011
| PositiveSequenceCapacitance | Double | 0.0066(µF/km) | 0.0066
High Voltage Line | Name | Text | GAHANGA | GAHANGA
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | ELETEL | ELETEL
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 9.6km | 9.6
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 130kN | 130
| MaxElectricResitance | Double | 0.119(Ώ/km) | 0.119
| PositiveSequenceReactance | Double | 0.427(Ω/km) | 0.427
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119
| ZeroSequenceCapacitance | Double | 0.011(µf/km) | 0.011
| PositiveSequenceCapacitance | Double | 0.0066(µF/km) | 0.0066
High Voltage Line | Name | Text | GIKONDO | GIKONDO
| Year_of_commisioning | Short Integer | 1974 | 1974
| ContractorName | Text | SGEEM | SGEEM
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR,CU | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 5.2km | 5.2
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 130kN | 130
| MaxElectricResitance | Double | 0.119(Ώ/km) | 0.119
| PositiveSequenceReactance | Double | 0.427(Ω/km) | 0.427
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119
| ZeroSequenceCapacitance | Double | 0.011(µf/km) | 0.011
| PositiveSequenceCapacitance | Double | 0.0066(µF/km) | 0.0066
High Voltage Line | Name | Text | JABANA | JABANA
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | ELTEL | ELTEL
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 240/40 | 240/40
| ShieldWire | Short Integer | OPGW | OPGW
| ConductorType | Short Integer | ACSR,CU | ACSR,CU
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 8.4km | 8.4km
| CurrentCarryingCapacity | Double | 40MW | 40MW
| NominalBreakingLoad_KN | Double | 130kN | 130kN
| MaxElectricResitance | Double | 0.119(Ώ/km) | 0.119(Ώ/km)
| PositiveSequenceReactance | Double | 0.427(Ω/km) | 0.427(Ω/km)
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123(Ω/km)
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327(Ω/km)
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119(Ω/km)
| ZeroSequenceCapacitance | Double | 0.011(µf/km) | 0.011(µf/km)
| PositiveSequenceCapacitance | Double | 0.0066(µF/km) | 0.0066(µF/km)
Transformer Bay | Trx_Bay_ID | Text | E05 | E05
| Substation_ID | Text | MKGL-004 | MKGL-004
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 20MVA | 20
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SIEMENS-7UT612 | SIEMENS-7UT612
| Type_of_Back_up_relay | Text | Included in 7UT612 | Included in 7UT612
| Type_of_BCU_Bay_control_unit | Text | ABB - REF630 | ABB - REF630
Transformer Bay | Trx_Bay_ID | Text | E06 | E06
| Substation_ID | Text | MKGL-004 | MKGL-004
| Trx_Bay_Name | Text | TRANSFORMER 2 | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 20MVA | 20
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | ABB-RET630 | ABB-RET630
| Type_of_Back_up_relay | Text | Included in 7UT612 | Included in 7UT612
| Type_of_BCU_Bay_control_unit | Text | ABB - REF630 | ABB - REF630
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SIEMENS | SIEMENS
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 3HA49 | 3HA49
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 30kV | 30
| MaxContinuousOperatVolt_kV | Double | 36kV | 36
| RatedImpulseWithstandVol | Double | 170kV | 170
| PowerFrequencyWithstandVol | Double | 70kV | 70
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 1600A | 1600
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SIEMENS | SIEMENS
| CircuitBreakerID | Text | CB-MV2 | CB-MV2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 3HA49 | 3HA49
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 30kV | 30
| MaxContinuousOperatVolt_kV | Double | 36kV | 36
| RatedImpulseWithstandVol | Double | 170kV | 170
| PowerFrequencyWithstandVol | Double | 70kV | 70
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 1250A | 1250
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV1-1 | CT-MV1-1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV | 36
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 500-1000A | 1000
| Rated_Secondary_Current | Double | 1-1A | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 95kV | 95
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV1-2 | CT-MV1-2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 24kV | 24
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 1000-2000A | 2000
| Rated_Secondary_Current | Double | 1-1A | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 95kV | 95
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV3-1 | CT-MV3-1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50Hz
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 80-240-640A | 640
| Rated_Secondary_Current | Double | 1-1A | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 95kV | 95
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV3-2 | CT-MV3-2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 24kV | 24
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 80-240-640A | 640
| Rated_Secondary_Current | Double | 1-1A | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 95kV | 95
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV1-1 | VT-MV1-1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 70kV | 70
| RatedImpulseWithstandVol | Double | 170kV | 170
| RatedPrimaryVoltage_kV | Double | 30kV/√3 | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 100V/√3 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60VA | 60
| TertiaryVoltage_kV | Long Integer | NA | NA
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV1-2 | VT-MV1-2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38kV | 38
| RatedImpulseWithstandVol | Double | 95kV | 95
| RatedPrimaryVoltage_kV | Double | 15kV/√3 | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100V/√3 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60VA | 60
| TertiaryVoltage_kV | Long Integer | NA | NA
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV3-1 | VT-MV3-1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 70kV | 70
| RatedImpulseWithstandVol | Double | 170kV | 170
| RatedPrimaryVoltage_kV | Double | 30kV/√3 | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 100V/√3 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60VA | 60
| TertiaryVoltage_kV | Long Integer | NA | NA
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV3-2 | VT-MV3-2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38kV | 38
| RatedImpulseWithstandVol | Double | 95kV | 95
| RatedPrimaryVoltage_kV | Double | 15kV/√3 | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100V/√3 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60VA | 60
| TertiaryVoltage_kV | Long Integer | NA | NA
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-002 | TSP-CPR-1-002
| Substation_ID | Text | MKGL-004 | MKGL-004
| Bay_ID | Text | E01 | E01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | 2010 | 2010
| Rated_Current | Double | 1-5A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-2-002 | TSP-CPR-2-002
| Substation_ID | Text | MKGL-004 | MKGL-004
| Bay_ID | Text | E02 | E02
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E02 | E02
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | 2010 | 2010
| Rated_Current | Double | 1-5A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-3-003 | TSP-CPR-3-003
| Substation_ID | Text | MKGL-004 | MKGL-004
| Bay_ID | Text | E03 | E03
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E03 | E03
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | 2010 | 2010
| Rated_Current | Double | 1-5A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-4-003 | TSP-CPR-4-003
| Substation_ID | Text | MKGL-004 | MKGL-004
| Bay_ID | Text | E04 | E04
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E04 | E04
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | 2010 | 2010
| Rated_Current | Double | 1-5A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | SIEMENS-7UT612 | SIEMENS-7UT612
| Bay_ID | Text | E05 | E05
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | SIEMENS-7UT612 | SIEMENS-7UT612
| Bay_ID | Text | E06 | E06
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E02 | E02
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E03 | E03
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E04 | E04
| Substatoin_ID | Text | MKGL-004 | MKGL-004
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| Standby_Generator_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Mode_Operation | Short Integer | Not existing
| Model | Text | Not existing
| Type_Assembly | Short Integer | Not existing
| Arrangement | Short Integer | Not existing
| Phases | Short Integer | Not existing
| RatedOuptuPower_kVA | Double | Not existing
| RatedVoltage | Double | Not existing
| RatedCurrent_A | Double | Not existing
| PowerFactor | Double | Not existing
| CouplingofEngine | Text | Not existing
| FuelLevelEmissionPerm | Double | Not existing
| DieselEngineType | Text | Not existing
| Governor | Text | Not existing
| GobernorBrand | Text | Not existing
| RatedPower_kVA_kW | Double | Not existing
| CompressionRatio_ | Text | Not existing
| NoofCylinder | Short Integer | Not existing
| Speed_RPM | Double | Not existing
| Applicable_Standard | Text | Not existing
| SpeedREgulation | Short Integer | Not existing
| Fuel_Tank_Capacity | Double | Not existing
| Cooling_System | Short Integer | Not existing
| NoiseatFullLoad | Double | Not existing
| LubricationOilConsumption | Double | Not existing
| Ambient_temperature | Double | Not existing
| Protection index | Text | Not existing
| MethodofStarting | Text | Not existing
| Voltage_VDC | Double | Not existing
| Power_kW | Double | Not existing
| Battery_Capacity_Ah | Double | Not existing
| BatteryType | Text | Not existing
| BrandandModelofBattery | Text | Not existing
| Frequency_Hz | Short Integer | Not existing
| VoltageRegulationMode | Short Integer | Not existing
| Total_Weight | Double | Not existing

## Sheet1
MONT KIGALI
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | MONT KIGALI | 23
| Substation_ID | Text | MKGL-004 | MKGL-004
| Substation_Total_Capacity_MVA | Double | 40MVA | 40
| Substation_Voltage_Level_kV | Short Integer | 110/30/15kV | 13
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 2 | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 1 | 1
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | No | 0
| Busbar_Configuration_HV | Short Integer | Single busbar | 1
| Number of MV Feeders | Short Integer | 11 | 11
| Number of HV line Bays | Short Integer | 4 | 4
| Number of Trx Bays | Short Integer | 2 | 2
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Tubular | 2
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2017 | 2017
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | ELTEL | ELTEL
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 0