## SHANGO SUBSTATION
SHANGO
Device | Field | Data Type | Domain | Domain Code
Power Transformer | transfomerID | Text | PTR-1-007 | PTR-1-007
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SNGO-007 | SNGO-007
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Year_commissioning | Short Integer | 2015 | 2015
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/110/11kV | 10
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 93.8MVA | 93.8
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 110kV | 110
| TertiaryCurrent_A | Short Integer | 11kV | 11
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 246.4A | 246.4
| SecondaryCurrent_A | Double | 493.4A | 493.4
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNyn0+d11 | 17
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 9.5% | 9.5
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 3
| No_Load_losses | Double | 65kW | 65
| LoadLosses | Double | 470kW | 470
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 25 | 25
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | 3XVMI501-170/C-14273W | 3XVMI501-170/C-14273W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text | 1565663 | 1565663
| Barcode | Text | NA | NA
| TotalWeight | Double | 123900kg | 123900
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 42900kg | 42900
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer | transfomerID | Text | PTR-2-007 | PTR-2-007
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SNGO-007 | SNGO-007
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Year_commissioning | Short Integer | 2015 | 2015
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/30kV | 2
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 31.5MVA | 31.5
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 30kV | 30
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 82.7A | 82.7
| SecondaryCurrent_A | Double | 165.5A | 165.5
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 9.5% | 9.5
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 40kW | 40
| LoadLosses | Double | 120kW | 120
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 33 | 33
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | UMIII350Y-72.5/C18353W | UMIII350Y-72.5/C18353W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2014 | 2014
| SerialNumber | Text | 1563775 | 1563775
| Barcode | Text | NA | NA
| TotalWeight | Double | 77000kg | 77000
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 21300kg | 21300
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer | transfomerID | Text | PTR-3-007 | PTR-3-007
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SNGO-007 | SNGO-007
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR3 | 2
| Manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Year_commissioning | Short Integer | 2015 | 2015
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/30kV | 2
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 31.5MVA | 31.5
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 30kV | 30k
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 82.7A | 82.7
| SecondaryCurrent_A | Double | 165.5A | 165.5
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | OUTDOOR
| PercentageImpedance | Double | 9.5% | 9.5
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | Copper
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 40kW | 40
| LoadLosses | Double | 120kW | 120
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 33 | 33
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | UMIII350Y-72.5/C18353W | UMIII350Y-72.5/C18353W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2014 | 2014
| SerialNumber | Text | 1563775 | 1563775
| Barcode | Text | NA | NA
| TotalWeight | Double | 77000kg | 77000
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 21300kg | 21300
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 0
Earthing Transformer | transfomerID | Text | ETR-TR1-007 | ETR-TR1-007
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SNGO-007 | SNGO-007
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR4 | 4
| Manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 11/0.4 | 4
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 0.315MVA | 0.315
| Primaryvoltage__kv | Double | 11kV | 11
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | Not Exising | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 16.5A | 16.5
| SecondaryCurrent_A | Double | 455.2A | 455.2
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | ZNyn11 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 4% | 4
| No_Load_losses | Double | 0.4kW | 0.4
| LoadLosses | Double | 5.2KW | 5.2
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 5 | 5
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | OFF LOAD | 2
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| Tap_changer_country_orgin_ | Text | INDIA | INDIA
| TapChangerManufacturingDate | Short Integer | 2015 | 2015
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 5220kg | 5220
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 212kg | 212
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 630A | 630
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2015 | 2015
Earthing Transformer | transfomerID | Text | ETR-TR1-007 | ETR-TR1-007
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SNGO-007 | SNGO-007
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR4 | 3
| Manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 30/0.4 | 1
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 0.315MVA | 0.315
| Primaryvoltage__kv | Double | 30kV | 30
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | Not Exising | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 6A | 6
| SecondaryCurrent_A | Double | 455.2A | 455.2
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | ZNyn11 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 4% | 4
| No_Load_losses | Double | 0.4kW | 0.4
| LoadLosses | Double | 5.2KW | 5.2
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 5 | 5
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | OFF LOAD | 2
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| Tap_changer_country_orgin_ | Text | INDIA | INDIA
| TapChangerManufacturingDate | Short Integer | 2015 | 2015
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 5220kg | 5220
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 212kg | 212
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 630A | 630
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2015 | 2015
Earthing Transformer | transfomerID | Text | ETR-TR1-007 | ETR-TR1-007
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SNGO-007 | SNGO-007
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR4 | 3
| Manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 30/0.4 | 1
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 0.315MVA | 0.315
| Primaryvoltage__kv | Double | 30kV | 30
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | Not Exising | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 6A | 6
| SecondaryCurrent_A | Double | 455.2A | 455.2
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | ZNyn11 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 4% | 4
| No_Load_losses | Double | 0.4kW | 0.4
| LoadLosses | Double | 5.2KW | 5.2
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 5 | 5
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | OFF LOAD | 2
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | CROMPTON GREAVES | CROMPTON GREAVES
| Tap_changer_country_orgin_ | Text | INDIA | INDIA
| TapChangerManufacturingDate | Short Integer | 2015 | 2015
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 5220kg | 5220
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 212kg | 212
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 630A | 630
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2015 | 2015
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | SNGO-007 | SNGO-007
| Busbar_HV_ID | Text | BB-007 | BB-007
| Number_of_Busbar_HV | Short Integer | 2 | 2
| Number_of_Busbar_MV | Short Integer | 2 | 2
| Type_of_Busbar | Short Integer | Conductor | Conductor
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | AAA | 4
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 220kV | 220
| Short_circuit_current_kA | Double | 50kA | 50
| Nominal_Current_A | Double | 1500A | 1500
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | SCHNEIDER - MICOM P746 | SCHNEIDER - MICOM P746
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K01 | K01
| FeederName | Text | INCOMER TR1 | INCOMER TR1
| PanelFunction | Short Integer | Incomer Feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | CB with isolator
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR840971-1 | TR840971-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000m
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K02 | K02
| FeederName | Text | OUTGOING FEEDER | OUTGOING FEEDER
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841003-1 | TR841003-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30KV
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K03 | K03
| FeederName | Text | OUTGOING FEEDER | OUTGOING FEEDER
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841035-1 | TR841035-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K04 | K04
| FeederName | Text | OUTGOING FEEDER | OUTGOING FEEDER
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841067-1 | TR841067-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K05 | K05
| FeederName | Text | OUTGOING FEEDER | OUTGOING FEEDER
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841099-1 | TR841099-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K06 | K06
| FeederName | Text | BUS COUPLER FEEDER | BUS COUPLER FEEDER
| PanelFunction | Short Integer | Busbar Feeder | 3
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | NA | NA
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841131-1 | TR841131-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | NA | NA
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K08 | K08
| FeederName | Text | OUTGOING FEEDER | OUTGOING FEEDER
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841200-1 | TR841200-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K09 | K09
| FeederName | Text | OUTGOING FEEDER | OUTGOING FEEDER
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841232-1 | TR841232-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-007 | SWG-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| FeederID | Text | K010 | K010
| FeederName | Text | INCOMER FEEDER | INCOMER FEEDER
| PanelFunction | Short Integer | Incomer Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2023 | 2023
| Serial_Number | Text | TR841264-1 | TR841264-1
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2023 | 2023
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | GHA | GHA
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | IEC 61850 | IEC 61850
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36.5kV | 36.5
| type_protection_relay | Short Integer | MICOM P139 | MICOM P139
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 630A | 630
| Rated_SF6_Pressure_Kpa | Double | 50kPa | 50
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | D01 | D01
| Substation_ID | Text | SNGO-007 | SNGO-007
| Line_Bay_Name | Text | MIRAMA 1 | MIRAMA 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264- | SCHNEIDER - MICOM C264-
Line Bay | Line_Bay_ID | Text | D02 | D02
| Substation_ID | Text | SNGO-007 | SNGO-007
| Line_Bay_Name | Text | MIRAMA 2 | MIRAMA 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264- | SCHNEIDER - MICOM C264-
Line Bay | Line_Bay_ID | Text | D03 | D03
| Substation_ID | Text | SNGO-007 | SNGO-007
| Line_Bay_Name | Text | RUBAVU 1 | RUBAVU 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264- | SCHNEIDER - MICOM C264-
Line Bay | Line_Bay_ID | Text | D07 | D07
| Substation_ID | Text | SNGO-007 | SNGO-007
| Line_Bay_Name | Text | BUGESERA 1 | BUGESERA 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIFANG - CSC 103 | SIFANG - CSC 103
| Type_of_Distance_relay | Text | SCHNEIDER - MICOM P443 | SCHNEIDER - MICOM P443
| Type_of_Back_up_relay | Text | SIFANG - CSC 211 | SIFANG - CSC 211
| Type_of_BCU_Bay_control_unit | Text | SIFANG - CSC 211 | SIFANG - CSC 211
Line Bay | Line_Bay_ID | Text | E01 | E01
| Substation_ID | Text | SNGO-007 | SNGO-007
| Line_Bay_Name | Text | BIREMBO 1 | BIREMBO 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264- | SCHNEIDER - MICOM C264-
Line Bay | Line_Bay_ID | Text | E02 | E02
| Substation_ID | Text | SNGO-007 | SNGO-007
| Line_Bay_Name | Text | BIREMBO 2 | BIREMBO 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264- | SCHNEIDER - MICOM C264-
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1 | VT2-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2 | VT2-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3 | VT2-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1 | VT3-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2 | VT3-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3 | VT3-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-1 | VT7-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-2 | VT7-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-3 | VT7-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-1 | VT11-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-2 | VT11-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-3 | VT11-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-11 | VT11-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-12 | VT11-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-13 | VT11-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT8-1 | VT8-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT8-2 | VT8-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT8-3 | VT8-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-1 | VT9-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1k
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-2 | VT9-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1k
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-3 | VT9-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1k
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT10-1 | VT10-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT10-2 | VT10-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT10-3 | VT10-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145V | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100734 | YHG 14100734
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100733 | YHG 14100733
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100746 | YHG 14100746
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D INDIA | GE T&D INDIA
| Current Transfomer ID | Text | CT1-11 | CT1-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 20VA | 20
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994027754 | 37994027754
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D INDIA | GE T&D INDIA
| Current Transfomer ID | Text | CT1-12 | CT1-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 20VA | 20
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994027755 | 37994027755
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D INDIA | GE T&D INDIA
| Current Transfomer ID | Text | CT1-13 | CT1-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 20VA | 20
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994027756 | 37994027756
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT2-1 | CT2-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100738 | YHG 14100738
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT2-2 | CT2-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100739 | YHG 14100739
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT2-3 | CT2-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100748 | YHG 14100748
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ALSTHOM | ALSTHOM
| Current Transfomer ID | Text | CT2-11 | CT2-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 504671 | 504671
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ALSTHOM | ALSTHOM
| Current Transfomer ID | Text | CT2-12 | CT2-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 504672 | 504672
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | ALSTHOM | ALSTHOM
| Current Transfomer ID | Text | CT2-13 | CT2-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 504673 | 504673
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100731 | YHG14100731
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100728 | YHG14100728
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100743 | YHG14100743
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| Current Transfomer ID | Text | CT7-1 | CT7-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900628 | 1900628
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| Current Transfomer ID | Text | CT7-2 | CT7-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900629 | 1900629
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| Current Transfomer ID | Text | CT7-3 | CT7-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900630 | 1900630
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | MLIAN-HUAYI | MLIAN-HUAYI
| Current Transfomer ID | Text | CT4-1 | CT4-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | HY2104008-01-001 | HY2104008-01-001
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double |  | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | MLIAN-HUAYI | MLIAN-HUAYI
| Current Transfomer ID | Text | CT4-2 | CT4-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | HY2011022-02-004 | HY2011022-02-004
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | MLIAN-HUAYI | MLIAN-HUAYI
| Current Transfomer ID | Text | CT4-3 | CT4-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2021 | 2021
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | HY2011022-02-006 | HY2011022-02-006
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D Inda | GE T&D Inda
| Current Transfomer ID | Text | CT4-11 | CT4-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2022 | 2022
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994042002 | 37994042002
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double |  | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D Inda | GE T&D Inda
| Current Transfomer ID | Text | CT4-12 | CT4-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2022 | 2022
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | HY2011022-02-004 | HY2011022-02-004
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D Inda | GE T&D Inda
| Current Transfomer ID | Text | CT4-13 | CT4-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2022 | 2022
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994042003 | 37994042003
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT5-1 | CT5-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100711 | YHG14100711
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 120%
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT5-2 | CT5-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100750 | YHG14100750
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 120%
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT5-3 | CT5-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100748 | YHG14100748
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 120%
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT6-11 | CT6-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100697 | YHG14100697
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT6-12 | CT6-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100687 | YHG14100687
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT6-13 | CT6-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100698 | YHG14100698
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT6-21 | CT6-21
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100704 | YHG14100704
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT6-22 | CT6-22
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100696 | YHG14100696
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT6-23 | CT6-23
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100691 | YHG14100691
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT8-1 | CT8-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100659 | YHG14100659
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT8-2 | CT8-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100666 | YHG14100666
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT8-3 | CT8-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100681 | YHG14100681
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT9-1 | CT9-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100664 | YHG14100664
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT9-2 | CT9-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100667 | YHG14100667
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT9-3 | CT9-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 300-600A | 300-600
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG14100660 | YHG14100660
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 223285 | 223285
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB2 | CB2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 223286 | 223286
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 223257 | 223257
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB4 | CB4
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 213027 | 213027
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D Inda | GE T&D Inda
| CircuitBreakerID | Text | CB41 | CB41
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 3271007310021001 | 3271007310021001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB5 | CB5
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 213024 | 213024
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB6 | CB6
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 213025 | 213025
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE Suzhou | GE Suzhou
| CircuitBreakerID | Text | CB7 | CB7
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 279783010003 | 279783010003
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB8 | CB8
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 7386-10-2032913/1 | 7386-10-2032913/1
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTOM | ALSTOM
| CircuitBreakerID | Text | CB9 | CB9
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 7386-10-2032913/1 | 7386-10-2032913/1
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1 | Q1-1
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-1 | Q2-1
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-21 | Q1-2
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-22 | Q2-2
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2 | Q9-2
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-31 | Q1-3
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHINT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-32 | Q2-3
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHINT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-3 | Q9-3
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | CHINT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-41 | Q1-4
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-42 | Q2-4
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-41 | Q1-41
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-41 | Q2-41
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2022 | 2022
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-51 | Q1-5
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-52 | Q2-5
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-61 | Q1-6
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-62 | Q2-6
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHiNT | CHiNT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-7 | Q1-7
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-7 | Q2-7
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-7 | Q9-7
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | SHANDOM TAKAI | SHANDOM TAKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-8 | Q1-8
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-8 | Q9-8
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-9 | Q1-9
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-9 | Q9-9
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-10 | Q1-10
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-10 | Q2-10
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-51 | Q1-51
| Substation | Text | SNGO-007 | SNGO-007
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2014 | 2014
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | SHANGO | 39
| Substation_ID | Text | SNGO-007 | SNGO-008
| Substation_Total_Capacity_MVA | Double | 196.8MVA | 196.8
| Substation_Voltage_Level_kV | Short Integer | 220/110/30kV | 1
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 4 | 4
| Numbe_of_Earthing_Transfomer | Short Integer | 2 | 2
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | YES | 1
| Busbar_Configuration_HV | Short Integer | Double busbar | 2
| Number of MV Feeders | Short Integer | 10 | 10
| Number of HV line Bays | Short Integer | 6 | 6
| Number of Trx Bays | Short Integer | 4 | 4
| Configuration_Busbar_MV | Short Integer | Double busbar | 2
| BuscouplerHV | Short Integer | YES | 1
| BuscouplerMV | Short Integer | YES | 1
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2018 | 2019
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | EUCL - TAIKAI - STEG INTERNATIONAL - CCC | EUCL - TAIKAI - STEG INTERNATIONAL - CCC
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | No | 0
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1250 | NPT1250
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | SNGO-007 | SNGO-008
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA2-1 | SA2-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA2-2 | SA2-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA2-3 | SA2-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-1 | SA3-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-2 | SA3-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-1 | SA4-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-2 | SA4-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-3 | SA4-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-11 | SA4-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-12 | SA4-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-13 | SA4-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA5-1 | SA5-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA5-2 | SA5-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA5-3 | SA5-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | Name plate in the Electrical field | Name plate in the Electrical field
| ManufacturerYear | Text | Name plate in the Electrical field | Name plate in the Electrical field
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA5-11 | SA5-11
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA5-12 | SA5-12
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA5-13 | SA5-13
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA8-1 | SA8-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA8-2 | SA8-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA8-3 | SA8-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA9-1 | SA9-1
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA9-2 | SA9-2
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA9-3 | SA9-3
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV | 102kV
| RatedVoltage_kV1 | Double | 110kV | 110kV
| NominalDischargeCurrent_kA | Double | 20kA | 20kA
| Rated_short_circuit_Current | Double | 31.5kA | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV | 650kV
| PowerFrequencyWithstandVol | Double | 230kV | 230kV
| RatedContinuousContinuous_kv | Double | 102kV | 102kV
| DischargeCounter | Short Integer | YES | YES
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947 | IEC 60439/60947
| BatteryFloatingVoltage | Double | 50V | 50
| RatedVoltage | Double | 48V | 48
| TenHrsRatingCapacity | Double | 275Ah | 275
| One_min_rating_Current_A | Double | 1375A | 1375
| MaximumVolatge_V | Double | 68V | 68
| MinimumVoltage_V | Double | 40V | 40
| MinimumVoltageperCell | Double | 1.2V | 1.2
| NumberofCells | Short Integer | 40 | 40
| BatteryFloatingVoltage | Double | 50 | 50
| BoostChargingVoltage | Double | 68V | 68
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 82A | 82
| SelfDischargeat_25oC | Double | 7% | 7%
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 33hrs | 33
DC Supply 110 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Model | Text | SBLE600-1 | SBLE600-1
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110V | 110
| TenHrsRatingCapacity | Double | 600Ah | 600
| One_min_rating_Current_A | Double | 1200A | 1200
| MaximumVolatge_V | Double | 127V | 127
| MinimumVoltage_V | Double | 82V | 82
| MinimumVoltageperCell | Double | 2V | 2
| Number_of_cells__No_ | Long Integer | 56 | 56
| BatteryFloatingVoltage | Double | 112.5V | 112.5
| BoostChargingVoltage | Double | 132.3V | 132.3
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 120A | 120
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | EMERSON Network power Is S.A.S | EMERSON Network power Is S.A.S
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | FRANCE | FRANCE
| Model | Text | CR120 | CR120
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | CE | CE
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 5.5kVA | 5.5k
| DC Output (Kw) | Double | 4.4kW | 4.4
| DC_Output_kV | Double | 48V | 48
| Rated_output_Voltage_V | Double | 48V | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ | 5
| OperatingConditions | Text | Continuous | Continuous
| Altitude_m | Double | 2000m | 2000
| Degree_protection_ | Short Integer | IP 20 | IP 20
| DCDistributionBoard | Short Integer | No | No
| RatedCurrent_A | Double | NA | NA
| NumberofFeeders | Short Integer | NA | NA
| short_circuit_capacity_breaker | Double | NA | NA
DC Supply 110 VDC charger | Manufacturer | Text | EMERSON Network power Is S.A.S | EMERSON Network power Is S.A.S
| Substation_ID | Text | SNGO-007 | SNGO-007
| CountryOfManufacturer | Text | FRANCE | FRANCE
| Model | Text | CR188-FP40R30 220 110C | CR188-FP40R30 220 110C
| TypeofOperation | Short Integer | Parallel | Parallel
| Charger_type | Short Integer | Thyristor controlled, | 2
| Standards_ | Text | IEC 61000-6-4 | IEC 61000-6-4
| ChargingTime | Double | 5h | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 30.5kVA | 30.5
| VoltageVariation | Double | ±5% | ±5%
| DC_Output_kV | Double | 110V | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110V | 110
| MaximumDC_Voltage_V | Double | 126V | 126
| ConstantVoltageAccuracy | Double | ±10% | ±10%
| Rated_DC_output_Current_A | Double | 166A | 166
| FloatingVoltageRegulatin | Double | 104.4V | 104.4
| EqualisingVoltageRegulatin | Double | 128.8V | 128.8
| Minimum_Insulation_resistance_ | Double | 5MΏ | 5
| TypeofCooling | Short Integer | Natural self-ventilating, Others | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C | 0°C to +40°C
| Altitude_m | Double | >1000m | 1000
| Total_Weight_Charger_kg | Double | 340kg | 340
| Degree_protection_ | Short Integer | IP20 | IP20
| RatedCurrent_A | Double | 100A | 100
| ShortCircuitStrength_kA_sec | Double | Not provided | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate | Copper tin-plate
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE | FRANCE
| Type | Text | REASON DR60 | REASON DR60
| Standards | Text | IEC61850 | IEC61850
| Arrangement | Short Integer | Panel mounted | Panel mounted
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A | 1A
| Nominal_voltage_Vdc | Double | 110DC | 110
| Power_consumption_VA | Double | 150VA | 150
| NumberofAnalogInputs | Short Integer | 32 | 32
| NumberofBinaryInputs | Short Integer | 96 | 96
| NumberofBinaryOutputs | Short Integer | 48 | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | MIRAMA 1 | MIRAMA 1
| Year_of_commisioning | Short Integer | 2016 | 2016
| ContractorName | Text | BOUYGUES | BOUYGUES
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 220
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 92.1km | 92.1
| CurrentCarryingCapacity | Double | 80MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | MIRAMA 2 | MIRAMA 2
| Year_of_commisioning | Short Integer | 2016 | 2016
| ContractorName | Text | BOUYGUES | BOUYGUES
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 220
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 92.1km | 92.1
| CurrentCarryingCapacity | Double | 80MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | RUBAVU 1 | RUBAVU 1
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | KALPATARU | KALPATARU
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 220
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 105km | 105km
| CurrentCarryingCapacity | Double | 80MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | Not yet construced | 0.0066
High Voltage Line | Name | Text | BUGESERA 1 | BUGESERA 1
| Year_of_commisioning | Short Integer | 2023 | 2023
| ContractorName | Text | JOHNSON POWER LTD | JOHNSON POWER LTD
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 220
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 34.2km | 34.2km
| CurrentCarryingCapacity | Double | 40MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | BIREMBO 1 | BIREMBO 1
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | KALPATARU | KALPATARU
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 110kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 9.6km | 9.6
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | BIREMBO 2 | BIREMBO 2
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | KALPATARU | KALPATARU
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 110kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 9.6km | 9.6
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
Transformer Bay | Trx_Bay_ID | Text | D04 | D04
| Substation_ID | Text | SNGO-007 | SNGO-007
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Trx_Bay_Capacity_MVA | Double | 31.5MVA | 31.5
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SCHNEIDER-MICOM P632 | SCHNEIDER-MICOM P632
| Type_of_Back_up_relay | Text | ABB-RET650 | ABB-RET650
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264 | SCHNEIDER - MICOM C264
Transformer Bay | Trx_Bay_ID | Text | D041 | D041
| Substation_ID | Text | SNGO-007 | SNGO-007
| Trx_Bay_Name | Text | TRANSFORMER 2 | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Trx_Bay_Capacity_MVA | Double | 31.5MVA | 31.5
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SCHNEIDER-MICOM P632 | SCHNEIDER-MICOM P632
| Type_of_Back_up_relay | Text | ABB-RET650 | ABB-RET650
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264 | SCHNEIDER - MICOM C264
Transformer Bay | Trx_Bay_ID | Text | D05 | D05
| Substation_ID | Text | SNGO-007 | SNGO-007
| Trx_Bay_Name | Text | TRANSFORMER 2 | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Trx_Bay_Capacity_MVA | Double | 93.8MVA | 93.8
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SCHNEIDER-MICOM P632 | SCHNEIDER-MICOM P632
| Type_of_Back_up_relay | Text | ABB-RET650 | ABB-RET650
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264 | SCHNEIDER - MICOM C264
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SCHNEIDER | SCHNEIDER
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | GHA 36-25-12 | GHA 36-25-12
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 30kV | 30
| MaxContinuousOperatVolt_kV | Double | 36kV | 36
| RatedImpulseWithstandVol | Double | 170kV | 170
| PowerFrequencyWithstandVol | Double | 70kV | 70
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 1250A | 1250
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25k
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | Yes
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SCHNEIDER | SCHNEIDER
| CircuitBreakerID | Text | CB-MV2 | CB-MV2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | GHA 36-25-12 | GHA 36-25-12
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 30kV | 30
| MaxContinuousOperatVolt_kV | Double | 36kV | 36
| RatedImpulseWithstandVol | Double | 170kV | 170
| PowerFrequencyWithstandVol | Double | 70kV | 70
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25k
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 630A | 630
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25k
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | Yes
Indoor Current Transformer | Manufacturer | Text | SCHNEIDER | SCHNEIDER
| CurrentTransfomer_ID | Text | CT-MV1 | CT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | CHA 250/81 CA | CHA 250/81 CA
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 30kV | 30
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 800-1600A | 800-1600
| Rated_Secondary_Current | Double | 1-1A | 1A
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 170kV | 170
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Current Transformer | Manufacturer | Text | SCHNEIDER | SCHNEIDER
| CurrentTransfomer_ID | Text | CT-MV2 | CT-MV2
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | CHA 250/81 CA | CHA 250/81 CA
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 30kV | 30
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1-1A | 1A
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 170kV | 170
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Voltage Transformer | Manufacturer | Text | RITZ | RITZ
| VoltageTransfomer_ID | Text | VT-MV1 | VT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | VGM 36 H | VGM 36 H
| Rated_Frequency | Short Integer | 50Hz | 50Hz
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38kV | 38
| RatedImpulseWithstandVol | Double | 70kV | 70
| RatedPrimaryVoltage_kV | Double | 15kV | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100V | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 15VA | 15
| TertiaryVoltage_kV | Long Integer |  | 0.1
Indoor Voltage Transformer | Manufacturer | Text | RITZ | RITZ
| VoltageTransfomer_ID | Text | VT-MV1 | VT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | VGM 36 H | VGM 36 H
| Rated_Frequency | Short Integer | 50Hz | 50Hz
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38kV | 38
| RatedImpulseWithstandVol | Double | 70kV | 70
| RatedPrimaryVoltage_kV | Double | 15kV | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100V | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 15VA | 15
| TertiaryVoltage_kV | Long Integer |  | 0.1
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-1-007 | TSP-CPR-1-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| Bay_ID | Text | D01 | D01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | D01 | D01
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 11
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-2-007 | TSP-CPR-2-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| Bay_ID | Text | D02 | D02
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-3-007 | TSP-CPR-3-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| Bay_ID | Text | D03 | D03
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | D03 | D03
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-4-007 | TSP-CPR-4-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| Bay_ID | Text | D07 | D07
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIFANG -CSC 103 | SIFANG -CSC 103
Distance Protection | RelayType | Text | SCHNEIDER - MICOM P443 | SCHNEIDER - MICOM P443
| Bay_ID | Text | D07 | D07
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAMD | ENGLAMD
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-5-007 | TSP-CPR-5-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| Bay_ID | Text | E01 | E01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | Yes
| FloorMounted | Short Integer | Yes | Yes
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5mm
| Max_height_mm | Double | 2000mm | 2000mm
| MaxWidth_mm | Double | 1500mm | 1500mm
| MaxDepth | Double | 2500mm | 2500mm
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-6-007 | TSP-CPR-6-007
| Substation_ID | Text | SNGO-007 | SNGO-007
| Bay_ID | Text | E02 | E02
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | E02 | E02
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | SCHNEIDER - MICOM P642 | SCHNEIDER - MICOM P642
| Bay_ID | Text | D04 | D04
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | SCHNEIDER - MICOM P642 | SCHNEIDER - MICOM P642
| Bay_ID | Text | D041 | D041
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | SCHNEIDER - MICOM P642 | SCHNEIDER - MICOM P642
| Bay_ID | Text | D05 | D05
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | D01 | D01
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | D03 | D03
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SIFANG - CSC 211 | SIFANG - CSC 211
| Bay_ID | Text | D07 | D07
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SIEFANG | SIEFANG
| Country_manufacturer_ | Text | CHINA | CHINA
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 1
| Phase to phase voltage (V) |  | 100V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | E02 | E02
| Substatoin_ID | Text | SNGO-007 | SNGO-007
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | GREEN POWER | GREEN POWER
| Substation_ID | Text | SNGO-007 | SNGO-007
| Standby_Generator_ID | Text | DGU-1-007 | DGU-1-007
| CountryOfManufacturer | Text | ITALY | ITALY
| Mode_Operation | Short Integer | Prime / Standby | Prime / Standby
| Model | Text | GP165 S/I-N-A | GP165 S/I-N-A
| Type_Assembly | Short Integer | Generating set ISO 8528 | Generating set ISO 8528
| Arrangement | Short Integer | Canopy type | Canopy type
| Phases | Short Integer | 3 | 3
| RatedOuptuPower_kVA | Double | 200kVA | 200
| RatedVoltage | Double | 230/400V | 400
| RatedCurrent_A | Double | 289A | 289
| PowerFactor | Double | 0.8 | 0.8
| CouplingofEngine | Text | Direct | Direct
| FuelLevelEmissionPerm | Double
| DieselEngineType | Text | Perkins | Perkins
| Governor | Text | PID | PID
| GobernorBrand | Text | Datakom (DKG) | Datakom (DKG)
| RatedPower_kVA_kW | Double | 200kVA | 200kVA
| CompressionRatio_ | Text | 15:01 | 15:01
| NoofCylinder | Short Integer | 6 | 6
| Speed_RPM | Double | 1500 | 1500
| Applicable_Standard | Text
| SpeedREgulation | Short Integer
| Fuel_Tank_Capacity | Double | 500L | 500
| Cooling_System | Short Integer | Liquid -cooled closed loup | Liquid -cooled closed loup
| NoiseatFullLoad | Double | 96dB | 96
| LubricationOilConsumption | Double | 0.025L/h | 0.025
| Ambient_temperature | Double | Minus 20 0C up to Plus 40 0C | Minus 20 0C up to Plus 40 0C
| Protection index | Text | IP44 | IP44
| MethodofStarting | Text | Man/Auto | Man/Auto
| Voltage_VDC | Double | 24V | 24
| Power_kW | Double | 160kW | 160
| Battery_Capacity_Ah | Double | 135Ah | 135
| BatteryType | Text | Lead-acid | Lead-acid
| BrandandModelofBattery | Text
| Frequency_Hz | Short Integer | 50Hz | 50
| VoltageRegulationMode | Short Integer | AVR | AVR
| Total_Weight | Double | 2110kg | 2110

## SUBSTATION SHEET
SHANGO
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | SHANGO | 39
| Substation_ID | Text | SNGO-007 | SNGO-008
| Substation_Total_Capacity_MVA | Double | 196.8MVA | 196.8
| Substation_Voltage_Level_kV | Short Integer | 220/110/30kV | 1
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 4 | 4
| Numbe_of_Earthing_Transfomer | Short Integer | 2 | 2
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | YES | 1
| Busbar_Configuration_HV | Short Integer | Double busbar | 2
| Number of MV Feeders | Short Integer | 10 | 10
| Number of HV line Bays | Short Integer | 6 | 6
| Number of Trx Bays | Short Integer | 4 | 4
| Configuration_Busbar_MV | Short Integer | Double busbar | 2
| BuscouplerHV | Short Integer | YES | 1
| BuscouplerMV | Short Integer | YES | 1
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2018 | 2019
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | EUCL - TAIKAI - STEG INTERNATIONAL - CCC | EUCL - TAIKAI - STEG INTERNATIONAL - CCC
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | No | 0