## SPLK SUBSTATION
SPLK
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-029 | PTR-1-029
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SPLK-029 | SPLK-029
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | SPECO | SPECO
| CountryOfManufacturer | Text | CHINA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Year_commissioning | Short Integer | 2021 | 2021
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/110 | 3
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 75MVA | 75
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 110kV | 110
| TertiaryCurrent_A | Short Integer | Not exixting | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 197A | 197
| SecondaryCurrent_A | Double | 3941A | 3941
| TertiaryCurrent_A | Double | Not existing | 0
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 9.5% | 9.5
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 3
| No_Load_losses | Double | 65kW | 65
| LoadLosses | Double | 470kW | 470
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 25 | 25
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | 3XVMI501-170/C-14273W | 3XVMI501-170/C-14273W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text
| Barcode | Text | NA | NA
| TotalWeight | Double | 123900kg | 123900
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 42900kg | 42900
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-029 | PTR-1-029
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | SPLK-029 | SPLK-029
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | SPECO | SPECO
| CountryOfManufacturer | Text | CHINA | INDIA
| ManufacturerYear | Short Integer | 2021 | 2021
| Year_commissioning | Short Integer | 2021 | 2021
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/110 | 3
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 75MVA | 75
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 110kV | 110
| TertiaryCurrent_A | Short Integer | Not exixting | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 197A | 197
| SecondaryCurrent_A | Double | 3941A | 3941
| TertiaryCurrent_A | Double | Not existing | 0
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 9.5% | 9.5
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 3
| No_Load_losses | Double | 65kW | 65
| LoadLosses | Double | 470kW | 470
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 25 | 25
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | 3XVMI501-170/C-14273W | 3XVMI501-170/C-14273W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text
| Barcode | Text | NA | NA
| TotalWeight | Double | 123900kg | 123900
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 42900kg | 42900
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | Not existing | Not existing
| PowerPlantID | Text | Not existing | Not existing
| Substation_ID | Text | Not existing | Not existing
| PowerPlantname | Text | Not existing | Not existing
| TransformerNaming | Short Integer | Not existing | Not existing
| Manufacturer | Text | Not existing | Not existing
| CountryOfManufacturer | Text | Not existing | Not existing
| ManufacturerYear | Short Integer | Not existing | Not existing
| Owner | Short Integer | Not existing | Not existing
| Primaryvoltage__kv | Double | Not existing | Not existing
| Secondaryvoltage__kv | Double | Not existing | Not existing
| TertiaryCurrent_A | Short Integer | Not existing | Not existing
| Nominal_Frequency | Short Integer | Not existing | Not existing
| PrimaryCurrent_A | Double | Not existing | Not existing
| SecondaryCurrent_A | Double | Not existing | Not existing
| TertiaryCurrent_A | Double | Not existing | Not existing
| Vector_Group_Trx | Short Integer | Not existing | Not existing
| CoolingMethod | Short Integer | Not existing | Not existing
| Phases | Short Integer | Not existing | Not existing
| WorkingCondition | Short Integer | Not existing | Not existing
| PercentageImpedance | Double | Not existing | Not existing
| No_Load_losses | Double | Not existing | Not existing
| LoadLosses | Double | Not existing | Not existing
| AltitudeLevel | Double | Not existing | Not existing
| Noiselevel_db | Double | Not existing | Not existing
| NumberOfTappingPosition | Short Integer | Not existing | Not existing
| Standard_Code | Text | Not existing | Not existing
| Tap_changer | Short Integer | Not existing | Not existing
| VoltageVariationRange1 | text | Not existing | Not existing
| Tap_changer_manufacturer | Text | Not existing | Not existing
| Tap_changer_country_orgin_ | Text | Not existing | Not existing
| TapChangerManufacturingDate | Short Integer | Not existing | Not existing
| SerialNumber | Text | Not existing | Not existing
| Barcode | Text | Not existing | Not existing
| TotalWeight | Double | Not existing | Not existing
| WeightOfActivePart | Double | Not existing | Not existing
| WeightOfOil | Double | Not existing | Not existing
| WeightOfUpperTank | Double | Not existing | Not existing
| TransportationOfWeight_N2 | Double | Not existing | Not existing
| WeightOfAccessories | Double | Not existing | Not existing
| LV_CB_A | Short Integer | Not existing | Not existing
| Earthing_Switch | Short Integer | Not existing | Not existing
| Notes | Text | Not existing | Not existing
| Branch | text | Not existing | Not existing
| Year_commissioning | Short Integer | Not existing | Not existing
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | SPLK-029 | SPLK-029
| Busbar_HV_ID | Text | BB-029 | BB-029
| Number_of_Busbar_HV | Short Integer | 2 | 2
| Number_of_Busbar_MV | Short Integer | 2 | 2
| Type_of_Busbar | Short Integer | Conductor | Conductor
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | AAA | 4
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 220kV | 220
| Short_circuit_current_kA | Double | 50kA | 50
| Nominal_Current_A | Double | 1500A | 1500
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | SCHNEIDER - MICOM P746 | SCHNEIDER - MICOM P746
MV Switch gear | SwitchGearID | Text | Not existing | Not existing
| Substation_ID | Text | Not existing | Not existing
| FeederID | Text | Not existing | Not existing
| FeederName | Text | Not existing | Not existing
| PanelFunction | Short Integer | Not existing | Not existing
| SwitchingDevices | Short Integer | Not existing | Not existing
| Type_of_MV_cable_termination | Short Integer | Not existing | Not existing
| Insulation_Medium | Short Integer | Not existing | Not existing
| Manufacturing_Year | Short Integer | Not existing | Not existing
| Serial_Number | Text | Not existing | Not existing
| Manufacturer | Text | Not existing | Not existing
| Year_of_Commissioning | Short Integer | Not existing | Not existing
| Country_origin | Text | Not existing | Not existing
| Type_Model | Text | Not existing | Not existing
| Altitude_m | Double | Not existing | Not existing
| Nominal_voltage_kV | Double | Not existing | Not existing
| Standards | Text | Not existing | Not existing
| Frequency_Hz | Short Integer | Not existing | Not existing
| Rated_voltage_kV | Double | Not existing | Not existing
| Maximum_continu_system_voltage | Double | Not existing | Not existing
| type_protection_relay | Short Integer | Not existing | Not existing
| Rated_short_circuit_current | Double | Not existing | Not existing
| Ratedpeak_shortcircuitcurrent | Double | Not existing | Not existing
| RatedBusbar_Current | Double | Not existing | Not existing
| Rated_SF6_Pressure_Kpa | Double | Not existing | Not existing
| Minimum_functional_level_for_SF6__KPa_ | Double | Not existing | Not existing
| Smart_meter_Installed | Short Integer | Not existing | Not existing
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | D01 | D01
| Substation_ID | Text | SPLK-029 | SPLK-029
| Line_Bay_Name | Text | RUBAVU | RUBAVU
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264 | SCHNEIDER - MICOM C264
Line Bay | Line_Bay_ID | Text | D02 | D02
| Substation_ID | Text | SPLK-029 | SPLK-029
| Line_Bay_Name | Text | BWISHYURA | BWISHYURA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
| Type_of_Distance_relay | Text | SEL 421 | SEL 421
| Type_of_Back_up_relay | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM C264 | SCHNEIDER - MICOM C264
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1 | VT2-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2 | VT2-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3 | VT2-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1 | VT3-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2 | VT3-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3 | VT3-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | CHINT ELECTRC | CHINT ELECTRC
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2015 | 2015
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100734 | YHG 14100734
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100733 | YHG 14100733
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100746 | YHG 14100746
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D INDIA | GE T&D INDIA
| Current Transfomer ID | Text | CT2-1 | CT2-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 20VA | 20
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994027754 | 37994027754
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D INDIA | GE T&D INDIA
| Current Transfomer ID | Text | CT2-2 | CT2-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 20VA | 20
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994027755 | 37994027755
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D INDIA | GE T&D INDIA
| Current Transfomer ID | Text | CT2-3 | CT2-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 20VA | 20
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994027756 | 37994027756
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100738 | YHG 14100738
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100739 | YHG 14100739
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2016 | 2016
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | YHG 14100748 | YHG 14100748
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT4-1 | CT4-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 504671 | 504671
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT4-2 | CT-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 504672 | 504672
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CHINT | CHINT
| Current Transfomer ID | Text | CT4-3 | CT4-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 504673 | 504673
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 120%
| PowerFrequencyTestVoltage_kV | Double | 530kV | 530
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB BEIJING | ABB BEIJING
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1361485926-01 | 1361485926-01
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 4000A | 4000
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 50
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 125A | 125
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.70MPa | 0.7
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3796kg | 3796
| TotalMassofInsulatingMed | Double | 36kg | 36
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB BEIJING | ABB BEIJING
| CircuitBreakerID | Text | CB2 | CB2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1361485926-01 | 1361485926-01
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 4000A | 4000
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 50
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 125A | 125
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.70MPa | 0.7
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3796kg | 3796
| TotalMassofInsulatingMed | Double | 36kg | 36
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB BEIJING | ABB BEIJING
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1361485926-01 | 1361485926-01
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 4000A | 4000
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 50
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 125A | 125
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.70MPa | 0.7
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3796kg | 3796
| TotalMassofInsulatingMed | Double | 36kg | 36
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB BEIJING | ABB BEIJING
| CircuitBreakerID | Text | CB4 | CB4
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2021 | 2021
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1361485926-01 | 1361485926-01
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 4000A | 4000
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 50
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 125A | 125
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.70MPa | 0.7
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3796kg | 3796
| TotalMassofInsulatingMed | Double | 36kg | 36
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1 | Q1-1
| Substation | Text | SPLK-029 | SPLK-029
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ABB JIANGSU | ABB JIANGSU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 2000A | 2000
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | RBVU-028 | RBVU-028
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | ABB JIANGSU | ABB JIANGSU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2 | Q1-2
| Substation | Text | SPLK-029 | SPLK-029
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ABB JIANGSU | ABB JIANGSU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 2000A | 2000
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2 | Q9-2
| Substation | Text | RBVU-028 | RBVU-028
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | ABB JIANGSU | ABB JIANGSU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3 | Q1-3
| Substation | Text | SPLK-029 | SPLK-029
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ABB JIANGSU | ABB JIANGSU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 2000A | 2000
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-4 | Q1-4
| Substation | Text | SPLK-029 | SPLK-029
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ABB JIANGSU | ABB JIANGSU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 2000A | 2000
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | SPLK | 58
| Substation_ID | Text | SPLK-029 | SPLK-029
| Substation_Total_Capacity_MVA | Double | 150MVA | 150
| Substation_Voltage_Level_kV | Short Integer | 220/11kV | 5
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 2 | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 0 | 0
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 0 | 0
| Standby_Generators | Short Integer | No | 0
| Busbar_Configuration_HV | Short Integer | Single Busbar | 1
| Number of MV Feeders | Short Integer | 0 | 0
| Number of HV line Bays | Short Integer | 2 | 2
| Number of Trx Bays | Short Integer | 2 | 2
| Configuration_Busbar_MV | Short Integer | No | 0
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Conductor | 1
| Type_of_MV_switchgears | Short Integer | No | 0
| Year of Commissioning | Short Integer | 2018 | 2019
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | REG | REG
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | No | 0
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1250 | NPT1250
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | SPLK-029 | SPLK-029
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA2-1 | SA2-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA2-2 | SA2-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-1 | SA3-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-2 | SA3-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-1 | SA4-1
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text | Name plate in the Electrical field | Name plate in the Electrical field
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-2 | SA4-2
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | CHINT | CHINT
| ArresterID | Text | SA4-3 | SA4-3
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2015 | 2015
| SerialNumber | Text
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text
| Country_orgin_Dis_Counter | Text
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947 | IEC 60439/60947
| BatteryFloatingVoltage | Double | 50V | 50
| RatedVoltage | Double | 48V | 48
| TenHrsRatingCapacity | Double | 275Ah | 275
| One_min_rating_Current_A | Double | 1375A | 1375
| MaximumVolatge_V | Double | 68V | 68
| MinimumVoltage_V | Double | 40V | 40
| MinimumVoltageperCell | Double | 1.2V | 1.2
| NumberofCells | Short Integer | 40 | 40
| BatteryFloatingVoltage | Double | 50 | 50
| BoostChargingVoltage | Double | 68V | 68
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 82A | 82
| SelfDischargeat_25oC | Double | 7% | 7%
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 33hrs | 33
DC Supply 110 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Model | Text | SBLE600-1 | SBLE600-1
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110V | 110
| TenHrsRatingCapacity | Double | 600Ah | 600
| One_min_rating_Current_A | Double | 1200A | 1200
| MaximumVolatge_V | Double | 127V | 127
| MinimumVoltage_V | Double | 82V | 82
| MinimumVoltageperCell | Double | 2V | 2
| Number_of_cells__No_ | Long Integer | 56 | 56
| BatteryFloatingVoltage | Double | 112.5V | 112.5
| BoostChargingVoltage | Double | 132.3V | 132.3
| FloatChargeCurrent_A | Double | 6.2A | 6.2
| BoostChargeCurrent | Double | 120A | 120
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | EMERSON Network power Is S.A.S | EMERSON Network power Is S.A.S
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | FRANCE | FRANCE
| Model | Text | CR120 | CR120
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | CE | CE
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 5.5kVA | 5.5k
| DC Output (Kw) | Double | 4.4kW | 4.4
| DC_Output_kV | Double | 48V | 48
| Rated_output_Voltage_V | Double | 48V | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ | 5
| OperatingConditions | Text | Continuous | Continuous
| Altitude_m | Double | 2000m | 2000
| Degree_protection_ | Short Integer | IP 20 | IP 20
| DCDistributionBoard | Short Integer | No | No
| RatedCurrent_A | Double | NA | NA
| NumberofFeeders | Short Integer | NA | NA
| short_circuit_capacity_breaker | Double | NA | NA
DC Supply 110 VDC charger | Manufacturer | Text | EMERSON Network power Is S.A.S | EMERSON Network power Is S.A.S
| Substation_ID | Text | SPLK-029 | SPLK-029
| CountryOfManufacturer | Text | FRANCE | FRANCE
| Model | Text | CR188-FP40R30 220 110C | CR188-FP40R30 220 110C
| TypeofOperation | Short Integer | Parallel | Parallel
| Charger_type | Short Integer | Thyristor controlled, | 2
| Standards_ | Text | IEC 61000-6-4 | IEC 61000-6-4
| ChargingTime | Double | 5h | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 30.5kVA | 30.5
| VoltageVariation | Double | ±5% | ±5%
| DC_Output_kV | Double | 110V | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110V | 110
| MaximumDC_Voltage_V | Double | 126V | 126
| ConstantVoltageAccuracy | Double | ±10% | ±10%
| Rated_DC_output_Current_A | Double | 166A | 166
| FloatingVoltageRegulatin | Double | 104.4V | 104.4
| EqualisingVoltageRegulatin | Double | 128.8V | 128.8
| Minimum_Insulation_resistance_ | Double | 5MΏ | 5
| TypeofCooling | Short Integer | Natural self-ventilating, Others | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C | 0°C to +40°C
| Altitude_m | Double | >1000m | 1000
| Total_Weight_Charger_kg | Double | 340kg | 340
| Degree_protection_ | Short Integer | IP20 | IP20
| RatedCurrent_A | Double | 100A | 100
| ShortCircuitStrength_kA_sec | Double | Not provided | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate | Copper tin-plate
DIGITAL fault recorder | Manufacturer | Text | Not existing | Not existing
| Country_Manufacture | Text | Not existing | Not existing
| Type | Text | Not existing | Not existing
| Standards | Text | Not existing | Not existing
| Arrangement | Short Integer | Not existing | Not existing
| VT_CT_Connection | Short Integer | Not existing | Not existing
| Frequency_Hz | Short Integer | Not existing | Not existing
| Nominal_input_current_A | Double | Not existing | Not existing
| Nominal_voltage_Vdc | Double | Not existing | Not existing
| Power_consumption_VA | Double | Not existing | Not existing
| NumberofAnalogInputs | Short Integer | Not existing | Not existing
| NumberofBinaryInputs | Short Integer | Not existing | Not existing
| NumberofBinaryOutputs | Short Integer | Not existing | Not existing
| Surge_withstand_capability_KV_ | Double | Not existing | Not existing
| Operating_temperature_oC | Double | Not existing | Not existing
High Voltage Line | Name | Text | RUBAVU | RUBAVU
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | KALPATARU -India | KALPATARU -India
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 220
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 56km | 92.1
| CurrentCarryingCapacity | Double | 80MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1193(Ω/km) | 0.1193
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | BWISHYURA | BWISHYURA
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | KALPATARU -India | KALPATARU -India
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 220
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 56km | 92.1
| CurrentCarryingCapacity | Double | 80MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1193(Ω/km) | 0.1193
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.123(Ω/km) | 0.123
| ZeroSequenceResistance | Double | 0.327(Ω/km) | 0.327
| ZeroSequenceReactance | Double | 1.119(Ω/km) | 1.119
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | Not existing | Not existing
| CircuitBreakerID | Text | Not existing | Not existing
| CountryOfManufacturer | Text | Not existing | Not existing
| Type__model | Text | Not existing | Not existing
| Standard | Text | Not existing | Not existing
| CombinedEArthBusbarDisc | Short Integer | Not existing | Not existing
| ArcQuenchingMedium | Short Integer | Not existing | Not existing
| Number_phases | Long Integer | Not existing | Not existing
| RatedVoltage_kV1 | Double | Not existing | Not existing
| MaxContinuousOperatVolt_kV | Double | Not existing | Not existing
| RatedImpulseWithstandVol | Double | Not existing | Not existing
| PowerFrequencyWithstandVol | Double | Not existing | Not existing
| Rated_Frequency | Short Integer | Not existing | Not existing
| Rated_short_time_withstand_current__kA_ | Text | Not existing | Not existing
| Rated_Peak_Short_Cir_Current | Double | Not existing | Not existing
| RatedNormalCurrent_A | Double | Not existing | Not existing
| RatedShortCircuitBreakCur_kA | Double | Not existing | Not existing
| RatedShortCircuitMakCurrent_A | Double | Not existing | Not existing
| RatedCableChargingBreakingCur | Double | Not existing | Not existing
| MaximumCApacitivBreakingCur | Double | Not existing | Not existing
| Rated_Operating_Sequence | Text | Not existing | Not existing
| ClosingTime_ms | Double | Not existing | Not existing
| DeadTime_ms | Double | Not existing | Not existing
| BreakTime_ms | Double | Not existing | Not existing
| MakeTime_ms | Double | Not existing | Not existing
| ArcingTime_ms | Double | Not existing | Not existing
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | Not existing | Not existing
| NumberofNc | Short Integer | Not existing | Not existing
| RatedMotorVoltage_VDC | Double | Not existing | Not existing
| NumberofMakingCoils | Short Integer | Not existing | Not existing
| NumberofTrippingCoils | Short Integer | Not existing | Not existing
| Volatge_VDC | Double | Not existing | Not existing
| PowerSupply | Short Integer | Not existing | Not existing
| HandOperatingFacility | Short Integer | Not existing | Not existing
Indoor Current Transformer | Manufacturer | Text | Not existing | Not existing
| CurrentTransfomer_ID | Text | Not existing | Not existing
|  |  | Not existing | Not existing
| CountryOfManufacturer | Text | Not existing | Not existing
| Type__model | Text | Not existing | Not existing
| Standard | Text | Not existing | Not existing
| RatedVoltage_kV1 | Double | Not existing | Not existing
| Rated_Frequency | Short Integer | Not existing | Not existing
| Number_phases | Long Integer | Not existing | Not existing
| NumberofCores | Short Integer | Not existing | Not existing
| Rated_Primary_Current_A | Double | Not existing | Not existing
| Rated_Secondary_Current | Double | Not existing | Not existing
| AccuracyClass | Text | Not existing | Not existing
| Burden_VA | Double | Not existing | Not existing
| RatedShortTimeWithstandCur | Double | Not existing | Not existing
| Rated_Peak_Short_Cir_Current | Double | Not existing | Not existing
| RatedImpulseWithstandVol | Double | Not existing | Not existing
| LimitsContPrimaryCurrency_A | Double | Not existing | Not existing
Indoor Voltage Transformer | Manufacturer | Text | Not existing | Not existing
| VoltageTransfomer_ID | Text | Not existing | Not existing
|  |  | Not existing | Not existing
| CountryOfManufacturer | Text | Not existing | Not existing
| Standard | Text | Not existing | Not existing
| TypeofVoltageTransformer | Short Integer | Not existing | Not existing
| Rated_Frequency | Short Integer | Not existing | Not existing
| Number_phases | Long Integer | Not existing | Not existing
| PowerFrequencyWithstandVol | Double | Not existing | Not existing
| RatedImpulseWithstandVol | Double | Not existing | Not existing
| RatedPrimaryVoltage_kV | Double | Not existing | Not existing
| Rated_secondary_voltage_winding_1__V_ | Text | Not existing | Not existing
| Rated_secondary_voltage_winding_2__V_ | Text | Not existing | Not existing
| Accuracy_class__measuring_ | Text | Not existing | Not existing
| Accuracy_class__protection_ | Text | Not existing | Not existing
| RatedOutput_VA | Double | Not existing | Not existing
| TertiaryVoltage_kV | Long Integer | Not existing | Not existing
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-1-007 | TSP-CPR-1-007
| Substation_ID | Text | SPLK-029 | SPLK-029
| Bay_ID | Text | D01 | D01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | D01 | D01
| Substatoin_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 11
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-2-007 | TSP-CPR-2-007
| Substation_ID | Text | SPLK-029 | SPLK-029
| Bay_ID | Text | D02 | D02
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER - MICOM P545 | SCHNEIDER - MICOM P545
Distance Protection | RelayType | Text | SEL 421 | SEL 421
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | SCHWEITZER ENGINEERING | SCHWEITZER ENGINEERING
| Country_manufacturer_ | Text | USA | USA
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | SCHNEIDER - MICOM P632 | SCHNEIDER - MICOM P632
| Bay_ID | Text | D03 | D03
| Substatoin_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | SCHNEIDER - MICOM P632 | SCHNEIDER - MICOM P632
| Bay_ID | Text | D04 | D04
| Substatoin_ID | Text | SPLK-029 | SPLK-029
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | D01 | D01
| Substatoin_ID | Text | RBVU-028 | RBVU-028
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | SCHNEIDER - MICOM P141 | SCHNEIDER - MICOM P141
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | RBVU-028 | RBVU-028
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 1A | 1
| Phase current (A) |  | 50Hz | 50
| Phase to phase voltage (V) |  | 110V | 110
| Auxiliary voltage (V DC) |  | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Included in Power Plant | Included in Power Plant
| Substation_ID | Text | Included in Power Plant | Included in Power Plant
| Standby_Generator_ID | Text | Included in Power Plant | Included in Power Plant
| CountryOfManufacturer | Text | Included in Power Plant | Included in Power Plant
| Mode_Operation | Short Integer | Included in Power Plant | Included in Power Plant
| Model | Text | Included in Power Plant | Included in Power Plant
| Type_Assembly | Short Integer | Included in Power Plant | Included in Power Plant
| Arrangement | Short Integer | Included in Power Plant | Included in Power Plant
| Phases | Short Integer | Included in Power Plant | Included in Power Plant
| RatedOuptuPower_kVA | Double | Included in Power Plant | Included in Power Plant
| RatedVoltage | Double | Included in Power Plant | Included in Power Plant
| RatedCurrent_A | Double | Included in Power Plant | Included in Power Plant
| PowerFactor | Double | Included in Power Plant | Included in Power Plant
| CouplingofEngine | Text | Included in Power Plant | Included in Power Plant
| FuelLevelEmissionPerm | Double | Included in Power Plant | Included in Power Plant
| DieselEngineType | Text | Included in Power Plant | Included in Power Plant
| Governor | Text | Included in Power Plant | Included in Power Plant
| GobernorBrand | Text | Included in Power Plant | Included in Power Plant
| RatedPower_kVA_kW | Double | Included in Power Plant | Included in Power Plant
| CompressionRatio_ | Text | Included in Power Plant | Included in Power Plant
| NoofCylinder | Short Integer | Included in Power Plant | Included in Power Plant
| Speed_RPM | Double | Included in Power Plant | Included in Power Plant
| Applicable_Standard | Text | Included in Power Plant | Included in Power Plant
| SpeedREgulation | Short Integer | Included in Power Plant | Included in Power Plant
| Fuel_Tank_Capacity | Double | Included in Power Plant | Included in Power Plant
| Cooling_System | Short Integer | Included in Power Plant | Included in Power Plant
| NoiseatFullLoad | Double | Included in Power Plant | Included in Power Plant
| LubricationOilConsumption | Double | Included in Power Plant | Included in Power Plant
| Ambient_temperature | Double | Included in Power Plant | Included in Power Plant
| Protection index | Text | Included in Power Plant | Included in Power Plant
| MethodofStarting | Text | Included in Power Plant | Included in Power Plant
| Voltage_VDC | Double | Included in Power Plant | Included in Power Plant
| Power_kW | Double | Included in Power Plant | Included in Power Plant
| Battery_Capacity_Ah | Double | Included in Power Plant | Included in Power Plant
| BatteryType | Text | Included in Power Plant | Included in Power Plant
| BrandandModelofBattery | Text | Included in Power Plant | Included in Power Plant
| Frequency_Hz | Short Integer | Included in Power Plant | Included in Power Plant
| VoltageRegulationMode | Short Integer | Included in Power Plant | Included in Power Plant
| Total_Weight | Double | Included in Power Plant | Included in Power Plant