## BUGESERA SUBSTATION
BUGESERA
Device | Field | Data Type | Domain | Domain Code
Power Transformer | transfomerID | Text | PTR-1-011 | PTR-1-011
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | BGSR-011 | BGSR-011
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Year_commissioning | Short Integer | 2019 | 2019
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/110/11kV | 10
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 93.8MVA | 93.8
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 110kV | 110
| TertiaryCurrent_A | Short Integer | 11kV | 11
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 246.4A | 246.4
| SecondaryCurrent_A | Double | 493.4A | 493.4
| TertiaryCurrent_A | Double | 4929 | 4929
| Vector_Group_Trx | Short Integer | YN0d11 | 18
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 9.5% | 0.095
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 65kW | 65
| LoadLosses | Double | 470kW | 470
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 25 | 25
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | 3XVMI501-170/C-14273W | 3XVMI501-170/C-14273W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text | 2120046 | 2120046
| Barcode | Text | NA | NA
| TotalWeight | Double | 125100kg | 125100
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 37500kg | 37500
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer | transfomerID | Text | PTR-2-011 | PTR-2-011
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | BGSR-011 | BGSR-011
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | SANBIAN | SANBIAN
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Year_commissioning | Short Integer | 2019 | 2019
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 220/110/11kV | 10
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 93.8MVA | 93.8
| Primaryvoltage__kv | Double | 220 kV | 220
| Secondaryvoltage__kv | Double | 110kV | 110
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 246.4A | 246.4
| SecondaryCurrent_A | Double | 493.4A | 493.4
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YN0d11 | 18
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 9.5% | 0.095
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 65kW | 65
| LoadLosses | Double | 470kW | 470
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | 3XVMI501-170/C-14273W | 3XVMI501-170/C-14273W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text | 2120046 | 2120046
| Barcode | Text | NA | NA
| TotalWeight | Double | 115150kg | 115150
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 37300kg | 37300
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer | transfomerID | Text | PTR-3-011 | PTR-3-011
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | BGSR-011 | BGSR-011
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR3 | 1
| Manufacturer | Text | HANGZHOU | HANGZHOU
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2020 | 2020
| Year_commissioning | Short Integer | 2020 | 2020
| AssetGroup | Long Integer | Power Transformer | 12
| AssetType | Short Integer | 110/30kV | 2
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 20MVA | 20
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 30 kV | 30
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 105A | 105
| SecondaryCurrent_A | Double | 385A | 385
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YN0d11 | 18
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 9.5% | 0.095
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 20kW | 20kW
| LoadLosses | Double | 150kW | 150kW
| AltitudeLevel | Double | 2000m | 2000m
| Noiselevel_db | Double | 75dB | 75dB
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | On-load
| TapChangerModel | Text | C MIII-500Y/170C-14271W | C MIII-500Y/170C-14271W
| TappingRange | Double | 220±16% | 220±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2020 | 2020
| SerialNumber | Text | M200557 | M200557
| Barcode | Text | NA | NA
| TotalWeight | Double | 49100kg | 49100
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 14120kg | 14120
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | ETR-1-011 | ETR-1-011
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | BGSR-011 | BGSR-011
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR4 | 3
| Manufacturer | Text | JIANGSHANYUANGUANG | JIANGSHANYUANGUANG
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 30kV | Attribute not given
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double
| Primaryvoltage__kv | Double | 30kV | 30
| Secondaryvoltage__kv | Double | Not Exising | Not Exising
| TertiaryCurrent_A | Short Integer | Not Exising | Not Exising
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 52.4A | 52.4
| SecondaryCurrent_A | Double | NA | NA
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | ZN | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 4% | 0.04
| No_Load_losses | Double | 10kW | 10
| LoadLosses | Double | 25kW | 25
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 0 | 0
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | OFF LOAD | 2
| VoltageVariationRange1 | text | 30±2.5% | 30±2.5%
| Tap_changer_manufacturer | Text | JIANGSHANYUANGUANG | JIANGSHANYUANGUANG
| Tap_changer_country_orgin_ | Text | CHINA | CHINA
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 8920kg | 8920
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 1750kg | 1750
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | NA | NA
| Earthing_Switch | Short Integer | NA | 0
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2019 | 2019
Distribution Transformer | transfomerID | Text | AUX-TR1-011 | AUX-TR1-011
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | BGSR-011 | BGSR-011
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR5 | 4
| Manufacturer | Text | ZHJIANG CHINA | ZHJIANG CHINA
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| AssetGroup | Long Integer | Power Transformer | 12
| AssetType | Short Integer | 30/0.4kV | 1
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 0.315 MVA | 0.315
| Primaryvoltage__kv | Double | 30kV | 30
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | Not Exising | Not Exising
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 6A | 6
| SecondaryCurrent_A | Double | 455A | 455
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | Dyn11 | 13
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 5 | 5
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 4% | 0.04
| No_Load_losses | Double | 0.4kW | 0.4
| LoadLosses | Double | 5.2KW | 5.2
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 3 | 5
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer | OFF LOAD | 2
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | JIANGSHANYUANGUANG | JIANGSHANYUANGUANG
| Tap_changer_country_orgin_ | Text | CHINA | CHINA
| TapChangerManufacturingDate | Short Integer | 2019 | 2019
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 1730kg | 1730
| WeightOfActivePart | Double | Not provided | Not provided
| WeightOfOil | Double | 370kg | 370
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 630A | 630
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 1987 | 1987
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | BGSR-011 | BGSR-011
| Busbar_HV_ID | Text | BB-011 | BB-011
| Number_of_Busbar_HV | Short Integer | 2 | 2
| Number_of_Busbar_MV | Short Integer | 2 | 2
| Type_of_Busbar | Short Integer | Tubular | Tubular
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | Aluminium | 1
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 220kV | 220
| Short_circuit_current_kA | Double | 50kA | 50
| Nominal_Current_A | Double | 960A | 960
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H01 | H01
| FeederName | Text | AUXILIARY TR1 | AUXILIARY TR1
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1648 | 19Cb1648
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H02 | H02
| FeederName | Text | LINE 1 | LINE 1
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1649 | 19Cb1649
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30KV
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H03 | H03
| FeederName | Text | LINE 2 | LINE 2
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1650 | 19Cb1650
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30KV
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H4 | H4
| FeederName | Text | LINE 3 | LINE 3
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1651 | 19Cb1651
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30KV
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H05 | H05
| FeederName | Text | INCOMER TR 3 | INCOMER TR 3
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1652 | 19Cb1652
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H06 | H06
| FeederName | Text | BUS SECTION | BUS SECTION
| PanelFunction | Short Integer | Busbar feeder | 3
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | NA
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1653 | 19Cb1653
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H07 | H07
| FeederName | Text | BUS RISER | BUS RISER
| PanelFunction | Short Integer | Busbar feeder | 3
| SwitchingDevices | Short Integer | CB with isolator | 2
| Type_of_MV_cable_termination | Short Integer | NA
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Jb1654 | 19Jb1654
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H08 | H08
| FeederName | Text | LINE 4 | LINE 4
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1655 | 19Cb1655
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30KV
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H09 | H09
| FeederName | Text | LINE 5 | LINE 5
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1656 | 19Cb1656
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30KV
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-011 | SWG-011
| Substation_ID | Text | BGSR-011 | BGSR-011
| FeederID | Text | H010 | H010
| FeederName | Text | INDISTRIAL PARK | INDISTRIAL PARK
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2019 | 2019
| Serial_Number | Text | 19Cb1657 | 19Cb1657
| Manufacturer | Text | CHANGZHOU - JIANGSU | CHANGZHOU - JIANGSU
| Year_of_Commissioning | Short Integer | 2019 | 2019
| Country_origin | Text | CHINA | CHINA
| Type_Model | Text | HVA - 40.5 | HVA - 40.5
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV | 30
| Maximum_continu_system_voltage | Double | 36kV | 36
| type_protection_relay | Short Integer | SIFANG - CSC 211 | SIFANG - CSC 211
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 40kPa | 40
| Minimum_functional_level_for_SF6__KPa_ | Double | 20kPa | 20
| Smart_meter_Installed | Short Integer | No | No
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | D01 | D01
| Substation_ID | Text | BGSR-011 | BGSR-011
| Line_Bay_Name | Text | SHANGO | SHANGO
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIFANG - CSC 103 | SIFANG - CSC 103
| Type_of_Distance_relay | Text | SCHNEIDER - MICOM P443 | SCHNEIDER - MICOM P443
| Type_of_Back_up_relay | Text | SIFANG - CSC 211 | SIFANG - CSC 211
| Type_of_BCU_Bay_control_unit | Text | SIFANG - CSC 211 | SIFANG - CSC 211
Line Bay | Line_Bay_ID | Text | D02 | D02
| Substation_ID | Text | BGSR-011 | BGSR-011
| Line_Bay_Name | Text | RUSUMO FALLS | RUSUMO FALLS
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIFANG - CSC 103 | SIFANG - CSC 103
| Type_of_Distance_relay | Text | SCHNEIDER - MICOM P443 | SCHNEIDER - MICOM P443
| Type_of_Back_up_relay | Text | SIFANG - CSC 211 | SIFANG - CSC 211
| Type_of_BCU_Bay_control_unit | Text | SIFANG - CSC 211 | SIFANG - CSC 211
Line Bay | Line_Bay_ID | Text | D03 | D03
| Substation_ID | Text | BGSR-011 | BGSR-011
| Line_Bay_Name | Text | RWABUSORO 1 | RWABUSORO 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500 | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430 | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500 | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | D03 | D03
| Substation_ID | Text | BGSR-011 | BGSR-011
| Line_Bay_Name | Text | RWABUSORO 2 | RWABUSORO 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 80MW | 80
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500 | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430 | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500 | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | E01 | E01
| Substation_ID | Text | BGSR-011 | BGSR-011
| Line_Bay_Name | Text | INDITRIAL PARK | INDITRIAL PARK
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500 | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87 | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430 | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500 | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | E03 | E03
| Substation_ID | Text | BGSR-011 | BGSR-011
| Line_Bay_Name | Text | GAHANGA | GAHANGA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMEMS - 7SD22 | SIEMEMS - 7SD22
| Type_of_Distance_relay | Text | Including in SIEMEMS - 7SD22 | Including in SIEMEMS - 7SD22
| Type_of_Back_up_relay | Text | EFACEC-TPU S430 | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500 | EFACEC-BCU500
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SHANDONG - TAIKAI | SHANDONG - TAIKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 50VA | 50
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SHANDONG - TAIKAI | SHANDONG - TAIKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 50VA | 50
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SHANDONG - TAIKAI | SHANDONG - TAIKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 50VA | 50
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1 | VT2-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SHANDONG - TAIKAI | SHANDONG - TAIKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 50VA | 50
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2 | VT2-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SHANDONG - TAIKAI | SHANDONG - TAIKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 50VA | 50
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3 | VT2-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SHANDONG - TAIKAI | SHANDONG - TAIKAI
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 50VA | 50
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1 | VT3-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2 | VT3-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3 | VT3-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-1 | VT4-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-2 | VT4-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-3 | VT4-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-1 | VT5-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-2 | VT5-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-3 | VT5-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-1
| Substation_ID | Text | BGSR-011
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-2
| Substation_ID | Text | BGSR-011
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-3
| Substation_ID | Text | BGSR-011
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT8-1 | VT8-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT8-2 | VT8-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT8-3 | VT8-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-1 | VT9-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-2 | VT9-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-3 | VT9-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | Copper
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT17-1 | VT17-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT17-2 | VT17-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT17-3 | VT17-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | GE T&D India LTD | GE T&D India LTD
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 145kV | 145
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,2 & Cl.3P | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900632 | 1900632
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900633 | 1900633
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900634 | 1900634
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT2-1 | CT2-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900640 | 1900640
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 120%
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT2-2 | CT2-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900639 | 1900639
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 120%
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT2-3 | CT2-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P10 | Cl 0.5-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900638 | 1900638
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994023739/2018 | 37994023739/2018
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994023738/2018 | 37994023738/2018
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 120%
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 400-800
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994023737/201 | 37994023737/201
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | CT DISMENTLED
| Current Transfomer ID | Text | CT4-1
| Substation_ID | Text | CT DISMENTLED
| CountryOfManufacturer | Text | CT DISMENTLED
| ManufacturerYear | Double | CT DISMENTLED
| Standard_Code | Text | CT DISMENTLED
| RatedOutput_VA | Double | CT DISMENTLED
| Primaryvoltage__kv | Double | CT DISMENTLED
| Secondaryvoltage__kv | Double | CT DISMENTLED
| AccuracyClass | Text | CT DISMENTLED
| MaxThermalOutput | Double | CT DISMENTLED
| InsulationLV_kV | Double | CT DISMENTLED
| Frequency_Hz | Short Integer | CT DISMENTLED | 50
| TemperatureRange | Double | CT DISMENTLED
| RatedVoltageFactor | Double | CT DISMENTLED
| NumberofCores | Short Integer | CT DISMENTLED
| Rated_Primary_Current_A | Double | CT DISMENTLED
| Rated_Secondary_Current | Double | CT DISMENTLED
| Burden_VA | Double | CT DISMENTLED
| RatedShortTime_CirCurrent_kA | Double | CT DISMENTLED
| Rated_Peak_Short_Cir_Current | Double | CT DISMENTLED
| KneePoint_V | Double | CT DISMENTLED
| SerialNumber | Text | CT DISMENTLED
| SF_ALF | Text | CT DISMENTLED
| LimitsContPrimaryCurrency_A | Double | CT DISMENTLED
| PowerFrequencyTestVoltage_kV | Double | CT DISMENTLED
| Insulator | Short Integer | CT DISMENTLED | 1
| Degree_of_Protection | Text | CT DISMENTLED
| RatedContThermCurrentFactor_A | Double | CT DISMENTLED
| DurationofShortCircuit_s | Double | CT DISMENTLED
| AltitudeLevel | Double | CT DISMENTLED
Current Transformer | Manufacturer | Text | CT DISMENTLED
| Current Transfomer ID | Text | CT4-2
| Substation_ID | Text | CT DISMENTLED
| CountryOfManufacturer | Text | CT DISMENTLED
| ManufacturerYear | Double | CT DISMENTLED
| Standard_Code | Text | CT DISMENTLED
| RatedOutput_VA | Double | CT DISMENTLED
| Primaryvoltage__kv | Double | CT DISMENTLED
| Secondaryvoltage__kv | Double | CT DISMENTLED
| AccuracyClass | Text | CT DISMENTLED
| MaxThermalOutput | Double | CT DISMENTLED
| InsulationLV_kV | Double | CT DISMENTLED
| Frequency_Hz | Short Integer | CT DISMENTLED | 50
| TemperatureRange | Double | CT DISMENTLED
| RatedVoltageFactor | Double | CT DISMENTLED
| NumberofCores | Short Integer | CT DISMENTLED
| Rated_Primary_Current_A | Double | CT DISMENTLED
| Rated_Secondary_Current | Double | CT DISMENTLED
| Burden_VA | Double | CT DISMENTLED
| RatedShortTime_CirCurrent_kA | Double | CT DISMENTLED
| Rated_Peak_Short_Cir_Current | Double | CT DISMENTLED
| KneePoint_V | Double | CT DISMENTLED
| SerialNumber | Text | CT DISMENTLED
| SF_ALF | Text | CT DISMENTLED
| LimitsContPrimaryCurrency_A | Double | CT DISMENTLED
| PowerFrequencyTestVoltage_kV | Double | CT DISMENTLED
| Insulator | Short Integer | CT DISMENTLED | 1
| Degree_of_Protection | Text | CT DISMENTLED
| RatedContThermCurrentFactor_A | Double | CT DISMENTLED
| DurationofShortCircuit_s | Double | CT DISMENTLED
| AltitudeLevel | Double | CT DISMENTLED
Current Transformer | Manufacturer | Text | CT DISMENTLED
| Current Transfomer ID | Text | CT4-3
| Substation_ID | Text | CT DISMENTLED
| CountryOfManufacturer | Text | CT DISMENTLED
| ManufacturerYear | Double | CT DISMENTLED
| Standard_Code | Text | CT DISMENTLED
| RatedOutput_VA | Double | CT DISMENTLED
| Primaryvoltage__kv | Double | CT DISMENTLED
| Secondaryvoltage__kv | Double | CT DISMENTLED
| AccuracyClass | Text | CT DISMENTLED
| MaxThermalOutput | Double | CT DISMENTLED
| InsulationLV_kV | Double | CT DISMENTLED
| Frequency_Hz | Short Integer | CT DISMENTLED | 50
| TemperatureRange | Double | CT DISMENTLED
| RatedVoltageFactor | Double | CT DISMENTLED
| NumberofCores | Short Integer | CT DISMENTLED
| Rated_Primary_Current_A | Double | CT DISMENTLED
| Rated_Secondary_Current | Double | CT DISMENTLED
| Burden_VA | Double | CT DISMENTLED
| RatedShortTime_CirCurrent_kA | Double | CT DISMENTLED
| Rated_Peak_Short_Cir_Current | Double | CT DISMENTLED
| KneePoint_V | Double | CT DISMENTLED
| SerialNumber | Text | CT DISMENTLED
| SF_ALF | Text | CT DISMENTLED
| LimitsContPrimaryCurrency_A | Double | CT DISMENTLED
| PowerFrequencyTestVoltage_kV | Double | CT DISMENTLED
| Insulator | Short Integer | CT DISMENTLED | 1
| Degree_of_Protection | Text | CT DISMENTLED
| RatedContThermCurrentFactor_A | Double | CT DISMENTLED
| DurationofShortCircuit_s | Double | CT DISMENTLED
| AltitudeLevel | Double | CT DISMENTLED
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT5-1 | CT5-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 1000-2000A | 1000-2000
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900648 | 1900648
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT5-2 | CT5-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 1000-2000A | 1000-2000
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900647 | 1900647
| SF_ALF | Text | 5_10 | 5_10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP5
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT5-3 | CT5-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 1000-2000A | 1000-2000
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900646 | 1900646
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT6-1 | CT6-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 1000-2000A | 1000-2000
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900642 | 1900642
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT6-2 | CT6-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 1000-2000
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900643 | 1900643
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT6-3 | CT6-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 220kV | 220
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 400-800A | 1000-2000
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 1900652 | 1900652
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 460kV | 460
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT51-1 | CT51-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994025678/2019 | 37994025678/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT51-2 | CT51-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994025679/2019 | 37994025679/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT51-3 | CT51-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994025680/2019 | 37994025680/2019
| SF_ALF | Text | 5_10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT11-1 | CT11-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2020 | 2020
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000627 | 2000627
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT11-2 | CT11-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2020 | 2020
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000626 | 2000626
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT11-3 | CT11-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2020 | 2020
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000625 | 2000625
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT7-1 | CT7-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000622 | 2000622
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT7-2 | CT7-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000623 | 2000622
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT7-3 | CT7-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2018 | 2018
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000624 | 2000622
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT8-1 | CT8-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994029001/2019 | 37994029001/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT8-2 | CT8-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994029000/2019 | 37994029000/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT8-3 | CT8-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994028999/2019 | 37994028999/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT9-1 | CT9-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994025683/2019 | 37994025683/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT9-2 | CT9-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994025682/2019 | 37994025682/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | GE T&D | GE T&D
| Current Transfomer ID | Text | CT9-3 | CT9-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | India | India
| ManufacturerYear | Double | 2019 | 2019
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 37994025681/2019 | 37994025681/2019
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT12-1 | CT12-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2020 | 2020
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000630 | 2000630
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | Oil, Others
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT12-2 | CT12-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2020 | 2020
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000629 | 2000629
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | Oil, Others
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | SHANDONG TAIKAI | SHANDONG TAIKAI
| Current Transfomer ID | Text | CT12-3 | CT12-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Double | 2020 | 2020
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA | 30
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.2-5P10 | Cl 0.2-5P10
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 600-1200A | 600-1200
| Rated_Secondary_Current | Double | 1A | 1
| Burden_VA | Double | 30VA | 30
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 2000628 | 2000628
| SF_ALF | Text | 10 | 10
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | Oil, Others
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3s
| AltitudeLevel | Double | 2000m | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 279783010002 | 279783010002
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75MPa
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CircuitBreakerID | Text | CB2 | CB2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 279783010001 | 279783010001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE&TD | GE&TD
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 32710047900080001 | 32710047900080001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE&TD | GE&TD
| CircuitBreakerID | Text | CB4 | CB4
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 32710047900010003 | 32710047900010003
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE&TD | GE&TD
| CircuitBreakerID | Text | CB5 | CB5
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 32710047900020006 | 32710047900020006
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE&TD | GE&TD
| CircuitBreakerID | Text | CB10 | CB10
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 279783020002 | 279783020002
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE SUZHOU | GE SUZHOU
| CircuitBreakerID | Text | CB6 | CB6
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 279783020001 | 279783020001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV | 220
| HighestSystemVoltage_kV | Double | 245kV | 245
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 1200kV | 1200
| PowerFrequencyWithstandVol | Double | 530kV | 530
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50kA | 50
| RatedShortCircuitMakCurrent_A | Double | 100A | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.75MPa | 0.75
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50m | 50
| MaximumMakingTime_ms | Double | 70m | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 3230kg | 3230
| TotalMassofInsulatingMed | Double | 30.8kg | 30.8
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D | GE T&D
| CircuitBreakerID | Text | CB51 | CB51
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 32710057370010001' | 32710057370010001'
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.74 Mpa | 0.74
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE ZUZHOU | GE ZUZHOU
| CircuitBreakerID | Text | CB11 | CB11
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CINA | CINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 307284020002' | 307284020002'
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE ZUZHOU | GE ZUZHOU
| CircuitBreakerID | Text | CB7 | CB7
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CINA | CINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 307284020003' | 307284020003'
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150A
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE ZUZHOU | GE ZUZHOU
| CircuitBreakerID | Text | CB12 | CB12
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CINA | CINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 30728402001 | 30728402001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D | GE T&D
| CircuitBreakerID | Text | CB8 | CB8
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 32710055890010001' | 32710055890010001'
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.74 Mpa | 0.74
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D | GE T&D
| CircuitBreakerID | Text | CB9 | CB9
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 32710057370020001' | 32710057370020001'
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.74 Mpa | 0.74
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10kA
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1 | Q1-1
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | NO
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-1 | Q2-1
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | NO
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2 | Q1-2
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | NO
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-2 | Q2-2
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | NO
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2 | Q9-2
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3 | Q1-3
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-3 | Q2-3
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-3 | Q9-3
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-4 | Q1-4
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-4 | Q2-4
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-4 | Q9-4
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-5 | Q1-5
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-5 | Q2-5
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-5 | Q9-5
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-6 | Q1-6
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-6 | Q2-6
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-6 | Q9-6
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-10 | Q1-10
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-10 | Q2-10
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-10 | Q9-10
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 220kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-51 | Q1-51
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-7 | Q1-7
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Groupe | GE Grid solutions
| CountryOfManufacturer | Text | CHINA | INDIA
| ManufacturerYear | Short Integer | 2020 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-8 | Q1-8
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-8 | Q9-8
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-9 | Q1-9
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 220
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-9 | Q9-9
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | GE Grid solutions | GE Grid solutions
| CountryOfManufacturer | Text | INDIA | INDIA
| ManufacturerYear | Short Integer | 2018 | 2018
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 220
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-11 | Q1-11
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 11
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-12 | Q1-12
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110V
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-12 | Q2-12
| Substation | Text | BGSR-011 | BGSR-011
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | TAIKAI Group | TAIKAI Group
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2019 | 2019
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | BUGESERA | 43
| Substation_ID | Text | BGSR-011 | BGSR-011
| Substation_Total_Capacity_MVA | Double | 206.6MVA | 206.6
| Substation_Voltage_Level_kV | Short Integer | 220/110/30kV | 1
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 3 | 3
| Numbe_of_Earthing_Transfomer | Short Integer | 1 | 1
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 1 | 1
| Standby_Generators | Short Integer | YES | 1
| Busbar_Configuration_HV | Short Integer | Double busbar | Double busbar
| Number of MV Feeders | Short Integer | 9 | 9
| Number of HV line Bays | Short Integer | 6 | 6
| Number of Trx Bays | Short Integer | 3 | 3
| Configuration_Busbar_MV | Short Integer | Single Busbar | 1
| BuscouplerHV | Short Integer | YES | 1
| BuscouplerMV | Short Integer | Not Existing | 0
| Type_of_Busbar_HV | Short Integer | Tubular | Tubular
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 2019 | 2019
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | STEG INTERNATIONAL / TAIKAI | STEG INTERNATIONAL / TAIKAI
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1200 | NPT1200
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | MKGW-025 | MKGW-025
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA1-1
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA1-2
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA1-3
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA2-1
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA2-2
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA2-3
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA3-1
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA3-2
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA3-3
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA4-1
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA4-2
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA4-3
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA5-1 | SA5-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA5-2 | SA5-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA5-3 | SA5-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Transformer | 2
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV | 275
| MaxContinuousOperatVolt_kV | Double | 190kV | 190
| RatedVoltage_kV1 | Double | 220kV | 220
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 950kV | 950
| PowerFrequencyWithstandVol | Double | 275kV | 275
| RatedContinuousContinuous_kv | Double | 195kV | 195
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA51-1 | SA51-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP56
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA51-2 | SA51-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP56
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA51-3 | SA51-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP56
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC
| ArresterID | Text | SA7-1
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP56
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC
| ArresterID | Text | SA7-2 | SA7-2
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP56
Lightning Arrester | Manufacturer | Short Integer | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| ArresterID | Text | SA7-3 | SA7-3
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Text | 2019 | 2019
| SerialNumber | Text | 276986 | 276986
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | `
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 10kA | 10
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JINGUAN ELECTRIC | JINGUAN ELECTRIC
| Country_orgin_Dis_Counter | Text | CHINA | CHINA
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | Analog
| ProtClassDischargeCounter | Text | IP55 | IP56
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA8-1
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field | 1
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field | 1
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field | 1
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field | 2
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA8-2
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field | 1
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field | 1
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field | 1
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field | 2
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA8-3
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field | 1
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field | 1
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field | 1
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field | 2
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA9-1
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field | 1
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field | 1
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field | 1
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field | 2
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA9-2
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field | 1
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field | 1
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field | 1
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field | 2
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
Lightning Arrester | Manufacturer | Short Integer | TAIKAI
| ArresterID | Text | SA9-3
| Substation_ID | Text | BGSR-011
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | Name Plate in the Electrical Field
| SerialNumber | Text | Name Plate in the Electrical Field
| Standard Code | Text | Name Plate in the Electrical Field
| FunctionType | Short Integer | Name Plate in the Electrical Field | 1
| Type_Surge_Arrester | Short Integer | Name Plate in the Electrical Field | 1
| Power_Frequency_Voltage_kV | Double | Name Plate in the Electrical Field
| MaxContinuousOperatVolt_kV | Double | Name Plate in the Electrical Field
| RatedVoltage_kV1 | Double | Name Plate in the Electrical Field
| NominalDischargeCurrent_kA | Double | Name Plate in the Electrical Field
| Rated_short_circuit_Current | Double | Name Plate in the Electrical Field
| Light_Impulse_Withsand_kV | Double | Name Plate in the Electrical Field
| PowerFrequencyWithstandVol | Double | Name Plate in the Electrical Field
| RatedContinuousContinuous_kv | Double | Name Plate in the Electrical Field
| DischargeCounter | Short Integer | Name Plate in the Electrical Field | 1
| manufacturer_Disch_Counter | Text | Name Plate in the Electrical Field
| Country_orgin_Dis_Counter | Text | Name Plate in the Electrical Field
| TypeDischargeCounter | Text | Name Plate in the Electrical Field
| CounterIndicDischargeCounter | Short Integer | Name Plate in the Electrical Field | 2
| ProtClassDischargeCounter | Text | Name Plate in the Electrical Field
DC Supply 48 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947 | IEC 60439/60947
| BatteryFloatingVoltage | Double | 56V | 56
| RatedVoltage | Double | 48V | 48
| TenHrsRatingCapacity | Double | 460Ah | 460
| One_min_rating_Current_A | Double | 2305A | 2305
| MaximumVolatge_V | Double | 51.2V | 51.2
| MinimumVoltage_V | Double | 32V | 32
| MinimumVoltageperCell | Double | 1V | 1
| NumberofCells | Short Integer | 40 | 40
| BatteryFloatingVoltage | Double | 56V | 56
| BoostChargingVoltage | Double | 60V | 60
| FloatChargeCurrent_A | Double | 4.5A | 4.5
| BoostChargeCurrent | Double | 138.2A | 138.2
| SelfDischargeat_25oC | Double | 7% | 7%
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 55hrs | 55
DC Supply 110 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Model | Text | KM300P | KM300P
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110V | 110
| TenHrsRatingCapacity | Double | 300Ah | 300
| One_min_rating_Current_A | Double | 200A | 200
| MaximumVolatge_V | Double | 142.6V | 142.6
| MinimumVoltage_V | Double | 92V | 92
| MinimumVoltageperCell | Double | 2V | 2
| Number_of_cells__No_ | Long Integer | 92 | 92
| BatteryFloatingVoltage | Double | 129.72V | 129.72
| BoostChargingVoltage | Double | 142.6V | 142.6
| FloatChargeCurrent_A | Double | 6A | 6
| BoostChargeCurrent | Double | 60A | 60
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | EFACEC | EFACEC
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | PORTUGAL | PORTUGAL
| Model | Text | CIB S Nº2 110V / 8×20A WITH miniPSM | CIB S Nº2 110V / 8×20A WITH miniPSM
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN41773 | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 0.96kVA | 0.96
| DC Output (Kw) | Double | 0.768kW | 0.768
| DC_Output_kV | Double | 48V | 48
| Rated_output_Voltage_V | Double | 48V | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000m | 2000
| Degree_protection_ | Short Integer | IP 20 | IP 20
| DCDistributionBoard | Short Integer | No | No
| RatedCurrent_A | Double | NA | NA
| NumberofFeeders | Short Integer | NA | NA
| short_circuit_capacity_breaker | Double | NA | NA
DC Supply 110 VDC charger | Manufacturer | Text | EFAPOWER | EFAPOWER
| Substation_ID | Text | BGSR-011 | BGSR-011
| CountryOfManufacturer | Text | PORTUGAL | PORTUGAL
| Model | Text | CIBS 110/ 8*20A | CIBS 110/ 8*20A
| TypeofOperation | Short Integer | Parallel | Parallel
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Text | IEC 61000-6-4 | IEC 61000-6-4
| ChargingTime | Double | 5h | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 17.3kVA | 17.3
| VoltageVariation | Double | ±5% | ±5%
| DC_Output_kV | Double | 110V | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110V | 110
| MaximumDC_Voltage_V | Double | 126V | 126
| ConstantVoltageAccuracy | Double | ±10% | ±10%
| Rated_DC_output_Current_A | Double | 100A | 100
| FloatingVoltageRegulatin | Double | 104.4V | 104.4
| EqualisingVoltageRegulatin | Double | 128.8V | 128.8
| Minimum_Insulation_resistance_ | Double | 5MΏ | 5
| TypeofCooling | Short Integer | Natural self-ventilating, Others | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C | 0°C to +40°C
| Altitude_m | Double | >1000m | 1000
| Total_Weight_Charger_kg | Double | 340kg | 340
| Degree_protection_ | Short Integer | IP20 | IP20
| RatedCurrent_A | Double | 100A | 100
| ShortCircuitStrength_kA_sec | Double | Not provided | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate, Others | Copper tin-plate
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE | FRANCE
| Type | Text | REASON DR60 | REASON DR60
| Standards | Text | IEC61850 | IEC61850
| Arrangement | Short Integer | Panel mounted | Panel mounted
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A | 1A
| Nominal_voltage_Vdc | Double | 110DC | 110
| Power_consumption_VA | Double | 150VA | 150
| NumberofAnalogInputs | Short Integer | 32 | 32
| NumberofBinaryInputs | Short Integer | 96 | 96
| NumberofBinaryOutputs | Short Integer | 48 | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | SHANGO | SHANGO
| Year_of_commisioning | Short Integer | 2023 | 2023
| ContractorName | Text | JOHNSON POWER LTD - India | JOHNSON POWER LTD - India
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 1
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 34.2km | 34.2
| CurrentCarryingCapacity | Double | 80MW | 80
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | RUSUMO FALLS | RUSUMO FALLS
| Year_of_commisioning | Short Integer | 2023 | 2023
| ContractorName | Text | JOHNSON POWER LTD - India | JOHNSON POWER LTD - India
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 1
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 83.4km | 83.4
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | RWABUSORO 1 | RWABUSORO 1
| Year_of_commisioning | Short Integer | 2019 | 2019
| ContractorName | Text | STEG INTERNATIONAL | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 1
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 39.9km | 39.9
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | RWABUSORO 2 | RWABUSORO 2
| Year_of_commisioning | Short Integer | 2019 | 2019
| ContractorName | Text | STEG INTERNATIONAL | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 1
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 39.9km | 39.9
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | INDISTRIAL PARK | INDISTRIAL PARK
| Year_of_commisioning | Short Integer | 2020 | 2020
| ContractorName | Text | STEG INTERNATIONAL | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 110kV | 2
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 23km | 23
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
High Voltage Line | Name | Text | GAHANGA | GAHANGA
| Year_of_commisioning | Short Integer | 2019 | 2019
| ContractorName | Text | STEG INTERNATIONAL | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 110kV | 2
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | No
| Underground_Cable_Size | Short Integer | NA | NA
| UG_Length_Km | Double | NA | NA
| Length_of_the_Line_ | Double | 17.1km | 17.1
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 69.44kN | 69.44
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0066(µF) | 0.0066
Transformer Bay | Trx_Bay_ID | Text | D05 | D05
| Substation_ID | Text | BGSR-011 | BGSR-011
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Trx_Bay_Capacity_MVA | Double | 93.8MVA | 93.8
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | EFACEC TPU T500 | EFACEC TPU T500
| Type_of_Back_up_relay | Text | SIEMENS 7UT613 | SIEMENS 7UT613
| Type_of_BCU_Bay_control_unit | Text | EFACEC BCU500 | EFACEC BCU500
Transformer Bay | Trx_Bay_ID | Text | D08 | D08
| Substation_ID | Text | RBSR-038 | RBSR-038
| Trx_Bay_Name | Text | TRANSFORMER 2 | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 25MVA | 25
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | EFACEC TPU T500 | EFACEC TPU T500
| Type_of_Back_up_relay | Text | SIEMENS 7UT613 | SIEMENS 7UT613
| Type_of_BCU_Bay_control_unit | Text | EFACEC BCU500 | EFACEC BCU500
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ChangZhou - Jiangsu - China | ChangZhou - Jiangsu - China
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | CHINA | CHINA
| Type__model | Text | HVA - 40.5 | HVA - 40.5
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | YES
| ArcQuenchingMedium | Short Integer | SF6 | 1
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 30kV | 30
| MaxContinuousOperatVolt_kV | Double | 36kV | 36
| RatedImpulseWithstandVol | Double | 170kV | 170
| PowerFrequencyWithstandVol | Double | 70kV | 70
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 630A | 630
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25k
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | Request Shutdown to access the Name Plate
| CurrentTransfomer_ID | Text | Request Shutdown to access the Name Plate
Request Shutdown to access the Name Plate
| CountryOfManufacturer | Text | Request Shutdown to access the Name Plate
| Type__model | Text | Request Shutdown to access the Name Plate
| Standard | Text | Request Shutdown to access the Name Plate
| RatedVoltage_kV1 | Double | Request Shutdown to access the Name Plate
| Rated_Frequency | Short Integer | Request Shutdown to access the Name Plate | 50
| Number_phases | Long Integer | Request Shutdown to access the Name Plate
| NumberofCores | Short Integer | Request Shutdown to access the Name Plate
| Rated_Primary_Current_A | Double | Request Shutdown to access the Name Plate
| Rated_Secondary_Current | Double | Request Shutdown to access the Name Plate
| AccuracyClass | Text | Request Shutdown to access the Name Plate
| Burden_VA | Double | Request Shutdown to access the Name Plate
| RatedShortTimeWithstandCur | Double | Request Shutdown to access the Name Plate
| Rated_Peak_Short_Cir_Current | Double | Request Shutdown to access the Name Plate
| RatedImpulseWithstandVol | Double | Request Shutdown to access the Name Plate
| LimitsContPrimaryCurrency_A | Double | Request Shutdown to access the Name Plate
Indoor Voltage Transformer | Manufacturer | Text | Request Shutdown to access the Name Plate
| VoltageTransfomer_ID | Text | Request Shutdown to access the Name Plate
Request Shutdown to access the Name Plate
| CountryOfManufacturer | Text | Request Shutdown to access the Name Plate
| Standard | Text | Request Shutdown to access the Name Plate
| TypeofVoltageTransformer | Short Integer | Request Shutdown to access the Name Plate
| Rated_Frequency | Short Integer | Request Shutdown to access the Name Plate | 50
| Number_phases | Long Integer | Request Shutdown to access the Name Plate
| PowerFrequencyWithstandVol | Double | Request Shutdown to access the Name Plate
| RatedImpulseWithstandVol | Double | Request Shutdown to access the Name Plate
| RatedPrimaryVoltage_kV | Double | Request Shutdown to access the Name Plate
| Rated_secondary_voltage_winding_1__V_ | Text | Request Shutdown to access the Name Plate
| Rated_secondary_voltage_winding_2__V_ | Text | Request Shutdown to access the Name Plate
| Accuracy_class__measuring_ | Text | Request Shutdown to access the Name Plate
| Accuracy_class__protection_ | Text | Request Shutdown to access the Name Plate
| RatedOutput_VA | Double | Request Shutdown to access the Name Plate
| TertiaryVoltage_kV | Long Integer | Request Shutdown to access the Name Plate
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-1-038 | TSP-CPR-1-038
| Substation_ID | Text | BGSR-011 | BGSR-011
| Bay_ID | Text | D01 | D01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIFANG -CSC 103 | SIFANG -CSC 103
Distance Protection | RelayType | Text | SCHNEIDER - MICOM P443 | SCHNEIDER - MICOM P443
| Bay_ID | Text | D01 | D01
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-2-038 | TSP-CPR-2-038
| Substation_ID | Text | BGSR-011 | BGSR-011
| Bay_ID | Text | D02 | D02
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500 | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87 | SIEMENS 7SA87
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100-110V | 100V
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-3-038 | TSP-CPR-3-038
| Substation_ID | Text | BGSR-011 | BGSR-011
| Bay_ID | Text | D03 | D03
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500 | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87 | SIEMENS 7SA87
| Bay_ID | Text | D03 | D03
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100-110V | 100V
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-4-038 | TSP-CPR-4-038
| Substation_ID | Text | BGSR-011 | BGSR-011
| Bay_ID | Text | D04 | D04
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500 | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87 | SIEMENS 7SA87
| Bay_ID | Text | D04 | D04
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100-110V | 100V
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-5-038 | TSP-CPR-5-038
| Substation_ID | Text | BGSR-011 | BGSR-011
| Bay_ID | Text | E01 | E01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500 | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87 | SIEMENS 7SA87
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-6-038 | TSP-CPR-6-038
| Substation_ID | Text | BGSR-011 | BGSR-011
| Bay_ID | Text | E03 | E03
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500 | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87 | SIEMENS 7SA87
| Bay_ID | Text | E03 | E03
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1A | 1
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | EFACEC TPU T500 | EFACEC TPU T500
| Bay_ID | Text | D05 | D05
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | EFACEC TPU T500 | EFACEC TPU T500
| Bay_ID | Text | D10 | D10
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Transformer Protection | RelayType | Text | EFACEC TPU T500 | EFACEC TPU T500
| Bay_ID | Text | E04 | E04
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| SecondaryCurrent_A | Short Integer | 1A | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430 | EFACEC TPU S430
| Bay_ID | Text | D02 | D02
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430 | EFACEC TPU S430
| Bay_ID | Text | D03 | D03
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430 | EFACEC TPU S430
| Bay_ID | Text | D05 | D05
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430 | EFACEC TPU S430
| Bay_ID | Text | D06 | D06
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430 | EFACEC TPU S430
| Bay_ID | Text | D07 | D07
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430 | EFACEC TPU S430
| Bay_ID | Text | E02 | E02
| Substatoin_ID | Text | BGSR-011 | BGSR-011
| Manufacturer | Text | EFACEC | EFACEC
| Country_manufacturer_ | Text | PORTUGAL | PORTUGAL
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1A | 1
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | COMLERPOWER | COMLERPOWER
| Substation_ID | Text | BGSR-011 | BGSR-011
| Standby_Generator_ID | Text | DGU-1-011 | DGU-1-011
| CountryOfManufacturer | Text | CHINA | CHINA
| Mode_Operation | Short Integer | Prime / Standby | Prime / Standby
| Model | Text | GP165 S/I-N-A | GP165 S/I-N-A
| Type_Assembly | Short Integer | Generating set ISO 8528 | Generating set ISO 8528
| Arrangement | Short Integer | Canopy type | Canopy type
| Phases | Short Integer | 3 | 3
| RatedOuptuPower_kVA | Double | 250kVA | 250
| RatedVoltage | Double | 230/400V | 400
| RatedCurrent_A | Double | 361A | 361
| PowerFactor | Double | 0.8 | 0.8
| CouplingofEngine | Text | Direct | Direct
| FuelLevelEmissionPerm | Double
| DieselEngineType | Text | Perkins | Perkins
| Governor | Text | PID | PID
| GobernorBrand | Text | Datakom (DKG) | Datakom (DKG)
| RatedPower_kVA_kW | Double | 200kVA | 200
| CompressionRatio_ | Text | 15:01 | 15:01
| NoofCylinder | Short Integer | 6 | 6
| Speed_RPM | Double | 1500 | 1500
| Applicable_Standard | Text
| SpeedREgulation | Short Integer
| Fuel_Tank_Capacity | Double | 500L | 500
| Cooling_System | Short Integer | Liquid -cooled closed loup | Liquid -cooled closed loup
| NoiseatFullLoad | Double | 96dB | 96dB
| LubricationOilConsumption | Double | 0.025L/h | 0.025
| Ambient_temperature | Double | Minus 20 0C up to Plus 40 0C | Minus 20 0C up to Plus 40 0C
| Protection index | Text | IP44 | IP44
| MethodofStarting | Text | Man/Auto | Man/Auto
| Voltage_VDC | Double | 24V | 24
| Power_kW | Double | 160kW | 160
| Battery_Capacity_Ah | Double | 135Ah | 135
| BatteryType | Text | Lead-acid | Lead-acid
| BrandandModelofBattery | Text
| Frequency_Hz | Short Integer | 50Hz | 50
| VoltageRegulationMode | Short Integer | AVR | AVR
| Total_Weight | Double | 2200kg | 2200