## RWINKWAVU SUBSTATION
RWINKWAVU
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-017 | PTR-1-017
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | RKVU-017 | RKVU-017
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | TR1
| Manufacturer | Text | SHIHEN TECHN. Corporation | SHIHEN TECHN. Corporation
| CountryOfManufacturer | Text | JAPAN | JAPAN
| ManufacturerYear | Short Integer | 2013 | 2013
| Year_commissioning | Short Integer | 2013 | 2013
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 110/15kV | 5
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 6 MVA | 6
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 15kV | 15
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 31.5A | 31.5
| SecondaryCurrent_A | Double | 231.6A | 231.6
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | YNd11 | 14
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 9.95% | 9.95
| NoLoadCurr_Percentage | Double | 10% | 10
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 6.2kW | 6.2
| LoadLosses | Double | 52.4kW | 52.4
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 17 | 17
| TapChangerType | Short Integer | Onload | Onload
| TapChangerModel | Text | VIII200Y-76-10193G | VIII200Y-76-10193G
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2013 | 2013
| SerialNumber | Text | 1363173 | 1363173
| Barcode | Text | NA | NA
| TotalWeight | Double | 32000kG | 32000
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 12900kg | 12900
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | AUX-1-017 | AUX-1-017
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | RKVU-017 | RKVU-017
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | TR2
| Manufacturer | Text | SGB | SGB
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Short Integer | 2013 | 2013
| AssetGroup | Long Integer | Earthing Transformer | 13
| AssetType | Short Integer | 15/0.4kV | 2
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 0.160 MVA | 0.160 MVA
| Primaryvoltage__kv | Double | 15kV | 15
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 6.17A | 6.17
| SecondaryCurrent_A | Double | 231.2A | 231.2
| TertiaryCurrent_A | Double | NA | NA
| Vector_Group_Trx | Short Integer | Zyn11 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 2
| PercentageImpedance | Double | 4.3% | 4.3
| No_Load_losses | Double | 0.25kW | 0.25
| LoadLosses | Double | 0.5KW | 0.5
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 3 | 3
| Standard_Code | Text | IEC 76 | IEC 76
| Tap_changer | Short Integer | OFF LOAD | OFF LOAD
| VoltageVariationRange1 | text | 15kV±2.5% | 15kV±2.5%
| Tap_changer_manufacturer | Text | SGB | SGB
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2012 | 2012
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text | NA | NA
| TotalWeight | Double | 4210kg | 4210
| WeightOfActivePart | Double | Not provided | 0
| WeightOfOil | Double | 1260kg | 1260
| WeightOfUpperTank | Double | Not provided | 0
| TransportationOfWeight_N2 | Double | Not provided | 0
| WeightOfAccessories | Double | Not provided | 0
| LV_CB_A | Short Integer | 400A | 400
| Earthing_Switch | Short Integer | NA | NA
| Notes | Text | NA | NA
| Branch | text | NA | NA
| Year_commissioning | Short Integer | 2013 | 2013
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | RKVU-017
| Busbar_HV_ID | Text | Not Existing (T-off Substation)
| Number_of_Busbar_HV | Short Integer | Not Existing
| Number_of_Busbar_MV | Short Integer | Not Existing
| Type_of_Busbar | Short Integer | Not Existing
| Phase_sequence | Short Integer | Not Existing
| Busbar_Material | Short Integer | Not Existing
| Barcode | Short Integer | Not Existing
| Operating_Voltage_Level_kV | Double | Not Existing
| Short_circuit_current_kA | Double | Not Existing
| Nominal_Current_A | Double | Not Existing
| Frequency_Hz | Short Integer | Not Existing
| Type_of_busbar_protection_relay_differential | Text | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-017 | SWG-017
| Substation_ID | Text | RKVU-017 | RKVU-017
| FeederID | Text | H01 | H01
| FeederName | Text | INCOMER TR1 | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | SF6
| Manufacturing_Year | Short Integer | 2013 | 2013
| Serial_Number | Text | 1VB4026660 | 1VB4026660
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2013 | 2013
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | ZX2 | ZX2
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 17.5kV | 17.5
| type_protection_relay | Short Integer | REF 542+ | REF 542+
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 130kPa | 130
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa | 100
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-017 | SWG-017
| Substation_ID | Text | RKVU-017 | RKVU-017
| FeederID | Text | H02 | H02
| FeederName | Text | AKAGERA | AKAGERA
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2013 | 2013
| Serial_Number | Text | 1VB4026671 | 1VB4026671
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2013 | 2013
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | ZX2 | ZX2
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 17.5kV | 17.5
| type_protection_relay | Short Integer | REF 542+ | REF 542+
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 130kPa | 130
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa | 100
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-017 | SWG-017
| Substation_ID | Text | RKVU-017 | RKVU-017
| FeederID | Text | H03 | H03
| FeederName | Text | REDEMI | REDEMI
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2013 | 2013
| Serial_Number | Text | 1VB4026672 | 1VB4026672
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2013 | 2013
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | ZX2 | ZX2
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 17.5kV | 17.5
| type_protection_relay | Short Integer | REF 542+ | REF 542+
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 130kPa | 130
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa | 100
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-017 | SWG-017
| Substation_ID | Text | RKVU-017 | RKVU-017
| FeederID | Text | H04 | H04
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | SF6
| Manufacturing_Year | Short Integer | 2013 | 2013
| Serial_Number | Text | 1VB4026673 | 1VB4026673
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2013 | 2013
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | ZX2 | ZX2
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 17.5kV | 17.5
| type_protection_relay | Short Integer | REF 542+ | REF 542+
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 130kPa | 130
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa | 100
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-017 | SWG-017
| Substation_ID | Text | RKVU-017 | RKVU-017
| FeederID | Text | H05 | H05
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2013 | 2013
| Serial_Number | Text | 1VB4026674 | 1VB4026674
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2013 | 2013
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | ZX2 | ZX2
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 17.5kV | 17.5
| type_protection_relay | Short Integer | REF 542+ | REF 542+
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 130kPa | 130
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa | 100
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-017 | SWG-017
| Substation_ID | Text | RKVU-017 | RKVU-017
| FeederID | Text | H06 | H06
| FeederName | Text | AUXILIARY TRANSFORMER | AUXILIARY TRANSFORMER
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2013 | 2013
| Serial_Number | Text | 1VB4026675 | 1VB4026675
| Manufacturer | Text | ABB | ABB
| Year_of_Commissioning | Short Integer | 2013 | 2013
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | ZX2 | ZX2
| Altitude_m | Double | 2000m | 2000
| Nominal_voltage_kV | Double | 30KV | 30
| Standards | Text | 60870-5-103 | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 15kV | 15
| Maximum_continu_system_voltage | Double | 17.5kV | 17.5
| type_protection_relay | Short Integer | REF 542+ | REF 542+
| Rated_short_circuit_current | Double | 25kA | 25
| Ratedpeak_shortcircuitcurrent | Double | 63kA | 63
| RatedBusbar_Current | Double | 1250A | 1250
| Rated_SF6_Pressure_Kpa | Double | 130kPa | 130
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa | 100
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | E01 | E01
| Substation_ID | Text | RKVU-017 | RKVU-017
| Line_Bay_Name | Text | MUSHA | MUSHA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 110
| Line_Bay_Capacity_MVA | Double | 40MW | 40
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | Not existing | Not existing
| Type_of_Distance_relay | Text | Not existing | Not existing
| Type_of_Back_up_relay | Text | Not existing | Not existing
| Type_of_BCU_Bay_control_unit | Text | Not existing | Not existing
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | RKVU-017 | RKVU-017
| Manufacturer | Text | TRENCH | TRENCH
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2013 | 2013
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 123kV | 123
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | RKVU-017 | RKVU-017
| Manufacturer | Text | TRENCH | TRENCH
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2013 | 2013
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 123kV | 123
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | RKVU-017 | RKVU-017
| Manufacturer | Text | TRENCH | TRENCH
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2013 | 2013
| Standard_Code | Text | IEC 60044-5/2004 | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV | 110
| HighestSystemVoltage_kV | Double | 123kV | 123
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m | 2000
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA | 100
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 0.1kV | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA | 1000
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV | 550
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | TRENCH | TRENCH
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Double | 2013 | 2013
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 27370/020-007 | 27370/020-007
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | TRENCH | TRENCH
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Double | 2013 | 2013
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 27370/020-008 | 27370/020-008
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
Current Transformer | Manufacturer | Text | TRENCH | TRENCH
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Double | 2013 | 2013
| Standard_Code | Text | IEC 60044-1/03 | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA | 40
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 120% | 1.2
| InsulationLV_kV | Double | 1kV | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 5A | 5
| Burden_VA | Double | 40VA | 40
| RatedShortTime_CirCurrent_kA | Double | 31.5kA | 31.5
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
| KneePoint_V | Double | NA | NA
| SerialNumber | Text | 27370/020-009 | 27370/020-009
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
| PowerFrequencyTestVoltage_kV | Double | 230kV | 230
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain | IP55
| RatedContThermCurrentFactor_A | Double | 120% | 1.2
| DurationofShortCircuit_s | Double | 3s | 3
| AltitudeLevel | Double | 2000m | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM | ALSTHOM
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Short Integer | 2013 | 2013
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 10305-20-2035520/5 | 10305-20-2035520/5
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV | 145
| HighestSystemVoltage_kV | Double | 170kV | 170
| Rated_Frequency | Short Integer | 50Hz | 50
| Nominal_Current_A | Double | 3150A | 3150
| RatedImpulseWithstandVol | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| DurationofShortCircuit_s | Double | 3s | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40
| RatedLineChargingCurrent_A | Double | 50A | 50
| RatedShortCircuitMakCurrent_A | Double | 100kA | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa | 0.64
| RatedMotorVoltage_VDC | Double | 110V | 110
| RatedSupplyVoltageofAuxCirc | Double | 110V | 110
| RatedSupplyVoltClosOpDevice | Double | 110V | 110
| MaximumBreakingTime_ms | Double | 50ms | 50
| MaximumMakingTime_ms | Double | 70ms | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000m | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA | 10
| Owner | Short Integer | REG | 1
| TotalMassCircuitbreaker_kg | Double | 1423.3kg | 1423.3
| TotalMassofInsulatingMed | Double | 8.3kg | 8.3
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | RKVU-017 | RKVU-017
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 2
| Manufacturer | Text | ALSTHOM | ALSTHOM
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2013 | 2013
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250A | 1250
| Operating_Voltage_kV | Double | 110kV | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC | 110
| Auxiliary_Contact_Curr_Rating | Double | 10A | 10
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC | 110
| Rated_Peak_Short_Cir_Current | Double | 80kA | 80
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | T-off Substaion | 2
| Substation_Name | Short Integer | KABARONDO | 38
| Substation_ID | Text | RKVU-017 | RKVU-017
| Substation_Total_Capacity_MVA | Double | 6MVA | 6
| Substation_Voltage_Level_kV | Short Integer | 110/15kV | 9
| SubstationArrangement | Short Integer | T-off Substaion | 2
| Number_of_Power_Transformers | Short Integer | 1 | 1
| Numbe_of_Earthing_Transfomer | Short Integer | 0 | 0
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 1 | 1
| Standby_Generators | Short Integer | No | 0
| Busbar_Configuration_HV | Short Integer | No Busbar (T-off Substation)
| Number of MV Feeders | Short Integer | 6 | 6
| Number of HV line Bays | Short Integer | 0 | 0
| Number of Trx Bays | Short Integer | 1 | 1
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Not Existing
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 1987 | 1988
| Year_of_upgrade | Short Integer | 1987 & 2013 | 1988 & 2013
| Contractor_Name | Text | FORCE DE L'EST-GTME-TAKAOKA | FORCE DE L'EST-GTME-TAKAOKA
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1200 | NPT1200
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | RKVU-017 | RKVU-017
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2013 | 2013
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV | 230
| MaxContinuousOperatVolt_kV | Double | 102kV | 102
| RatedVoltage_kV1 | Double | 110kV | 110
| NominalDischargeCurrent_kA | Double | 20kA | 20
| Rated_short_circuit_Current | Double | 31.5kA | 31.5
| Light_Impulse_Withsand_kV | Double | 650kV | 650
| PowerFrequencyWithstandVol | Double | 230kV | 230
| RatedContinuousContinuous_kv | Double | 102kV | 102
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | HITACH | HITACH
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | JAPAN | JAPAN
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| BatteryFloatingVoltage | Double | 56V | 56
| RatedVoltage | Double | 48V | 48
| TenHrsRatingCapacity | Double | 100Ah | 100
| One_min_rating_Current_A | Double | 500A | 500
| MaximumVolatge_V | Double | 64V | 64
| MinimumVoltage_V | Double | 40V | 40
| MinimumVoltageperCell | Double | 1.02V | 1.02
| NumberofCells | Short Integer | 42 | 42
| BatteryFloatingVoltage | Double | 56V | 56
| BoostChargingVoltage | Double | 68V | 68
| FloatChargeCurrent_A | Double | 1.2A | 1.2
| BoostChargeCurrent | Double | 30A | 30
| SelfDischargeat_25oC | Double | 0.7 | 0.7
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 5h | 5
DC Supply 110 VDC Battery | Manufacturer | Text | HITACHI | HITACHI
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | JAPAN | JAPAN
| Model | Text | MSJ-150 | MSJ-150
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110V | 110
| TenHrsRatingCapacity | Double | 150Ah | 150
| One_min_rating_Current_A | Double | 300A | 300
| MaximumVolatge_V | Double | 123.5V | 123.5
| MinimumVoltage_V | Double | 93.5V | 93.5
| MinimumVoltageperCell | Double | 1V | 1
| Number_of_cells__No_ | Long Integer | 112V | 112
| BatteryFloatingVoltage | Double | 126V | 126
| BoostChargingVoltage | Double | 151.2V | 151.2
| FloatChargeCurrent_A | Double | 3A | 3
| BoostChargeCurrent | Double | 30A | 30
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | HITACH CHEMICAL Co.Ltd | HITACH CHEMICAL Co.Ltd
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | JAPAN | JAPAN
| Model | Text | A0-34-48 50-2BD-MJ | A0-34-48 50-2BD-MJ
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN VDE 0558 | DIN VDE 0558
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 5.53kVA | 5.53
| DC Output (Kw) | Double | 2.88kW | 2.88
| DC_Output_kV | Double | 48V | 48
| Rated_output_Voltage_V | Double | 48V | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΩ | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000m | 2000
| Degree_protection_ | Short Integer | IP55 | IP55
| DCDistributionBoard | Short Integer | No | 0
| RatedCurrent_A | Double | NA | 0
| NumberofFeeders | Short Integer | NA | 0
| short_circuit_capacity_breaker | Double | NA | 0
DC Supply 110 VDC charger | Manufacturer | Text | HITACH CHEMICAL Co.Ltd | HITACH CHEMICAL Co.Ltd
| Substation_ID | Text | RKVU-017 | RKVU-017
| CountryOfManufacturer | Text | JAPAN | JAPAN
| Model | Text | A0-34-123 50-2BD-MJ | A0-34-123 50-2BD-MJ
| TypeofOperation | Short Integer | Parallel_standby | Parallel_standby
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Text | DIN VDE 0558 | DIN VDE 0558
| ChargingTime | Double | 5h | 5
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V | 400
| Rated_InputPower_kVA | Double | 20kVA | 20
| VoltageVariation | Double
| DC_Output_kV | Double | 110V | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110V | 110
| MaximumDC_Voltage_V | Double | 123V | 123
| ConstantVoltageAccuracy | Double
| Rated_DC_output_Current_A | Double | 100A | 100
| FloatingVoltageRegulatin | Double | 104.4 | 104.4
| EqualisingVoltageRegulatin | Double | 128.8 | 128.8
| Minimum_Insulation_resistance_ | Double | 5 | 5
| TypeofCooling | Short Integer | Natural self-ventilating | Natural self-ventilating
| Ambient_temperature | Double | 0°C to +40°C | 0°C to +40°C
| Altitude_m | Double | 1000 | 1000
| Total_Weight_Charger_kg | Double | 340kg | 340
| Degree_protection_ | Short Integer | IP55 | IP55
| RatedCurrent_A | Double | 100A | 100
| ShortCircuitStrength_kA_sec | Double | Not indicated | Not indicated
| BusbarMaterial | Short Integer | Copper | 1
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE | FRANCE
| Type | Text | REASON DR60 | REASON DR60
| Standards | Text | IEC61850 | IEC61850
| Arrangement | Short Integer | Panel mounted | Panel mounted
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A | 5
| Nominal_voltage_Vdc | Double | 110DC | 110
| Power_consumption_VA | Double | 150VA | 150
| NumberofAnalogInputs | Short Integer | 32 | 32
| NumberofBinaryInputs | Short Integer | 96 | 96
| NumberofBinaryOutputs | Short Integer | 48 | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | MUSHA-RWINKWAVU | MUSHA-RWINKWAVU
| Year_of_commisioning | Short Integer | 1959 | 1959
| ContractorName | Text | FORCE DE L'EST | FORCE DE L'EST
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 110kV | 110
| CondustorSize | Short Integer | 150/25 | 4
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 30.3Km | 30.3
| CurrentCarryingCapacity | Double | 40MW | 40
| NominalBreakingLoad_KN | Double | 130KN | 130
| MaxElectricResitance | Double | 0.1937(Ω/km) | 0.1937
| PositiveSequenceReactance | Double | 0.437(Ω/km) | 0.437
| PositiveSequenceResistance | Double | 0.231(Ω/km) | 0.231
| ZeroSequenceResistance | Double | 0.554(Ω/km) | 0.554
| ZeroSequenceReactance | Double | 1.430(Ω/km) | 1.43
| ZeroSequenceCapacitance | Double | 0.01(µF) | 0.01
| PositiveSequenceCapacitance | Double | 0.0063(µF) | 0.0063
Transformer Bay | Trx_Bay_ID | Text | E01 | E01
| Substation_ID | Text | RKVU-017 | RKVU-017
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 10MVA | 10
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | ABB-RET 630 | ABB-RET 630
| Type_of_Back_up_relay | Text | Included in RET 630 | Included in RET 630
| Type_of_BCU_Bay_control_unit | Text | ABB - REF 542+ | ABB - REF 542+
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | VD4X1712-25 | VD4X1712-25
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 15kV | 15
| MaxContinuousOperatVolt_kV | Double | 17.5kV | 17.5
| RatedImpulseWithstandVol | Double | 95kV | 95
| PowerFrequencyWithstandVol | Double | 38kV | 38
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 1250A | 1250
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB-MV3 | CB-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | VD4X1712-25 | VD4X1712-25
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 15kV | 15
| MaxContinuousOperatVolt_kV | Double | 17.5kV | 17.5
| RatedImpulseWithstandVol | Double | 95kV | 95
| PowerFrequencyWithstandVol | Double | 38kV | 38
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedNormalCurrent_A | Double | 1250A | 1250
| RatedShortCircuitBreakCur_kA | Double | 25kA | 25
| RatedShortCircuitMakCurrent_A | Double | 63kA | 63
| RatedCableChargingBreakingCur | Double | 50A | 50
| MaximumCApacitivBreakingCur | Double | 875A | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms | 60
| DeadTime_ms | Double | 300ms | 300
| BreakTime_ms | Double | 85ms | 85
| MakeTime_ms | Double | 70ms | 70
| ArcingTime_ms | Double | 15ms | 15
| AtRAtedContinuousCurrent | Double | Not existing | Not existing
| AtRAtedBreakingCurrent | Double | Not existing | Not existing
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110V | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110V | 110
| PowerSupply | Short Integer | 110V DC | 110
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | ELQ | ELQ
| CurrentTransfomer_ID | Text | CT-MV1 | CT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | SVA 188-220-75-P1 | SVA 188-220-75-P1
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 15kV | 15
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 400
| Rated_Secondary_Current | Double | 1 | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 170kV | 170
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Current Transformer | Manufacturer | Text | RITZ | RITZ
| CurrentTransfomer_ID | Text | CT-MV3 | CT-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | GIKS08-24 | GIKS08-24
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 17.5kV | 17.5
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 80-240-640A | 640
| Rated_Secondary_Current | Double | 150mV | 150
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 170kV | 170
| LimitsContPrimaryCurrency_A | Double | 120% | 1.2
Indoor Voltage Transformer | Manufacturer | Text | RITZ | RITZ
| VoltageTransfomer_ID | Text | VT-MV1 | VT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | VGM 24 H | VGM 24 H
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38kV | 38
| RatedImpulseWithstandVol | Double | 95kV | 95
| RatedPrimaryVoltage_kV | Double | 15kV | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100V | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V | 100
| Accuracy_class__measuring_ | Text | Cl 0.5 FS5 | Cl 0.5 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60VA | 60
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | RITZ | RITZ
| VoltageTransfomer_ID | Text | VT-MV3 | VT-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | VGM 24 H | VGM 24 H
| Rated_Frequency | Short Integer | 50Hz | 50Hz
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38kV | 38
| RatedImpulseWithstandVol | Double | 95kV | 95
| RatedPrimaryVoltage_kV | Double | 15kV | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100V | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100V | 100
| Accuracy_class__measuring_ | Text | Cl 0.5 FS5 | Cl 0.5 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60VA | 60
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-3-002 | TSP-CPR-3-002
| Substation_ID | Text | RKVU-017 | RKVU-017
| Bay_ID | Text | E01 | E01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm | 2.5
| Max_height_mm | Double | 2000mm | 2000
| MaxWidth_mm | Double | 1500mm | 1500
| MaxDepth | Double | 2500mm | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SCHNEIDER-MICOM P545 | SCHNEIDER-MICOM P545
Distance Protection | RelayType | Text | Included in MICOM P545 | Included in MICOM P545
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | RKVU-017 | RKVU-017
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1-5A | 5
| Rated_Voltage | Double | 100-110V | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | ABB RET630 | ABB RET630
| Bay_ID | Text | E02 | E02
| Substatoin_ID | Text | RKVU-017 | RKVU-017
| Manufacturer | Text | ABB | ABB
| Country_manufacturer_ | Text | GERMANY | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A | 5
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V | 110
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SCHNEIDER-MICOM P545 | Included in SCHNEIDER-MICOM P545
| Bay_ID | Text | E03 | E03
| Substatoin_ID | Text | RKVU-017 | RKVU-017
| Manufacturer | Text | SCHNEIDER | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND | ENGLAND
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A | 5
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| Standby_Generator_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Mode_Operation | Short Integer | Not existing
| Model | Text | Not existing
| Type_Assembly | Short Integer | Not existing
| Arrangement | Short Integer | Not existing
| Phases | Short Integer | Not existing
| RatedOuptuPower_kVA | Double | Not existing
| RatedVoltage | Double | Not existing
| RatedCurrent_A | Double | Not existing
| PowerFactor | Double | Not existing
| CouplingofEngine | Text | Not existing
| FuelLevelEmissionPerm | Double | Not existing
| DieselEngineType | Text | Not existing
| Governor | Text | Not existing
| GobernorBrand | Text | Not existing
| RatedPower_kVA_kW | Double | Not existing
| CompressionRatio_ | Text | Not existing
| NoofCylinder | Short Integer | Not existing
| Speed_RPM | Double | Not existing
| Applicable_Standard | Text | Not existing
| SpeedREgulation | Short Integer | Not existing
| Fuel_Tank_Capacity | Double | Not existing
| Cooling_System | Short Integer | Not existing
| NoiseatFullLoad | Double | Not existing
| LubricationOilConsumption | Double | Not existing
| Ambient_temperature | Double | Not existing
| Protection index | Text | Not existing
| MethodofStarting | Text | Not existing
| Voltage_VDC | Double | Not existing
| Power_kW | Double | Not existing
| Battery_Capacity_Ah | Double | Not existing
| BatteryType | Text | Not existing
| BrandandModelofBattery | Text | Not existing
| Frequency_Hz | Short Integer | Not existing
| VoltageRegulationMode | Short Integer | Not existing
| Total_Weight | Double | Not existing

## Sheet1
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | T-off Substaion | 2
| Substation_Name | Short Integer | KABARONDO | 38
| Substation_ID | Text | RKVU-017 | RKVU-017
| Substation_Total_Capacity_MVA | Double | 6MVA | 6
| Substation_Voltage_Level_kV | Short Integer | 110/15kV | 9
| SubstationArrangement | Short Integer | T-off Substaion | 2
| Number_of_Power_Transformers | Short Integer | 1 | 1
| Numbe_of_Earthing_Transfomer | Short Integer | 0 | 0
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 1 | 1
| Standby_Generators | Short Integer | No | 0
| Busbar_Configuration_HV | Short Integer | No Busbar (T-off Substation)
| Number of MV Feeders | Short Integer | 6 | 6
| Number of HV line Bays | Short Integer | 0 | 0
| Number of Trx Bays | Short Integer | 1 | 1
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Not Existing
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 1987 | 1988
| Year_of_upgrade | Short Integer | 1987 & 2013 | 1988 & 2013
| Contractor_Name | Text | FORCE DE L'EST-GTME-TAKAOKA | FORCE DE L'EST-GTME-TAKAOKA
| Substation_Meter_SN | Text | NA | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1