## GAHANGA SUBSTATION
GAHANGA
Device | Field | Data Type | Domain | Domain Code
Power Transformer | transfomerID | Text | PTR-1-005 | PTR-1-005
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GHNG-005 | GHNG-005
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | ETRA | ETRA
| CountryOfManufacturer | Text | SLOVENIA | SLOVENIA
| ManufacturerYear | Short Integer | 2017 | 2017
| Year_commissioning | Short Integer | 2017 | 2017
| AssetGroup | Long Integer | Power Transformer | 11
| AssetType | Short Integer | 110/15kV | 5
| Owner | Short Integer | REG | 1
| Rated_Power_MVA | Double | 20MVA | 20
| Primaryvoltage__kv | Double | 110kV | 110
| Secondaryvoltage__kv | Double | 15kV | 15
| TertiaryCurrent_A | Short Integer | 0 | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 107.7A | 107.7
| SecondaryCurrent_A | Double | 769.8A | 769.8
| TertiaryCurrent_A | Double | 0 | 0
| Vector_Group_Trx | Short Integer | Yyn0+d11 | 17
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | OUTDOOR
| PercentageImpedance | Double | 11% | 0.11
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | Copper
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 11kW | 11
| LoadLosses | Double | 59.97kW | 59.97
| AltitudeLevel | Double | 2000 | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | Onload | 1
| TapChangerModel | Text | MII350Y-170/B-14273G | MII350Y-170/B-14273G
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2017 | 2017
| SerialNumber | Text | 1822452 | 1822452
| Barcode | Text | NA | NA
| TotalWeight | Double | 44000kg | 44000
| WeightOfActivePart | Double | 12300kg | 12300
| WeightOfOil | Double | 10800kg | 10800
| WeightOfUpperTank | Double | 22500kg | 22500
| TransportationOfWeight_N2 | Double | 36500kg | 36500
| Height | Double | Not provided | 0
| Depth | Double | Not provided | 0
| Width | Double | Not provided | 0
| Bushing_Material | Short Integer | Polcelain | 1
Distribution Transformer | transfomerID | Text | ETR-1-005 | ETR-1-005
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GHNG-005 | GHNG-005
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | NEWTON | NEWTON
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| AssetGroup | Long Integer | Distribution Transformer | 12
| AssetType | Short Integer | 15/30kV | 2
| Owner | Short Integer | REG | REG
| Rated_Power_MVA | Double | 0.160MVA | 0.16
| Primaryvoltage__kv | Double | 15kV | 15
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | NA | NA
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 3.85A | 3.85
| SecondaryCurrent_A | Double | 144.5A | 144.5
| TertiaryCurrent_A | Double
| Vector_Group_Trx | Short Integer | Dyn11 | 13
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 0.4 | 0.4
| No_Load_losses | Double | 320kW | 320
| LoadLosses | Double | 1750kW | 1750
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 55dB | 55
| NumberOfTappingPosition | Short Integer | 5 | 5
| Standard_Code | Text | IEC 60076 | IEC 60076
| Tap_changer | Short Integer
| VoltageVariationRange1 | text | 15±2.5% | 15±2.5%
| Tap_changer_manufacturer | Text | NEWTON | NEWTON
| Tap_changer_country_orgin_ | Text | ITALY | ITALY
| TapChangerManufacturingDate | Short Integer | 2017 | 2017
| SerialNumber | Text | Incorporated in Transformer | Incorporated in Transformer
| Barcode | Text
| TotalWeight | Double | 570kg | 570
| WeightOfActivePart | Double | Not provised | 0
| WeightOfOil | Double | 120kg | 120
| WeightOfUpperTank | Double | Not provised | 0
| TransportationOfWeight_N2 | Double | Not provised | 0
| WeightOfAccessories | Double | Not provised | 0
| LV_CB_A | Short Integer | 250A | 250
| Earthing_Switch | Short Integer | NA | 0
| Notes | Text | NA | 0
| Branch | text | NA | 0
| Year_commissioning | Short Integer | 2019 | 2019
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | GHNG-005 | GHNG-005
| Busbar_HV_ID | Text | BB-005 | BB-005
| Number_of_Busbar_HV | Short Integer | 1 | 1
| Number_of_Busbar_MV | Short Integer | 1 | 1
| Type_of_Busbar | Short Integer | Tubular | Tubular
| Phase_sequence | Short Integer | 7 | 7
| Busbar_Material | Short Integer | 3 | 1
| Barcode | Short Integer | NA | NA
| Operating_Voltage_Level_kV | Double | 110 | 110
| Short_circuit_current_kA | Double | 50 | 50
| Nominal_Current_A | Double | 960 | 960
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K01 | K01
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | 2 | 2
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000060/001 | CV917470-000060/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K02 | K02
| FeederName | Text | SPARE | SPARE
| PanelFunction | Short Integer | 2 | 2
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000050/001 | CV917470-000050/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K03 | K03
| FeederName | Text | PYLONE 20 | PYLONE 20
| PanelFunction | Short Integer | 2 | 2
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000080/001 | CV917470-000080/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K04 | K04
| FeederName | Text | GAHANGA STADIUM | GAHANGA STADIUM
| PanelFunction | Short Integer | 2 | 2
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000070/001 | CV917470-000070/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
Optical Telecommunication Equipment (Telecom) | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Country_manufacturer_ | Text | ISRAEL | ISRAEL
| Type | Short Integer | NPT1200 | NPT1200
| AssetGroup | Short Integer | Optical Telecommunication Equipment | 2
| AssetType | Short Integer | FO Multiplexer SDH (STM-16) and Access Multiplexer | 1
| MandatoryCardsorModules | Text | 10 | 10
| Redundant_power_supply_ | Double | YES | 1
| Power_supply_Vdc | Double | 48V | 48
| Power_consumption_W | Double | 1200W | 1200
| Current_A_ | Double | 25A | 25
ODF | Manufacturer | Text | ECI-RIBBON | ECI-RIBBON
| Substation_ID | Text | MKGW-025 | MKGW-025
| Country_manufacture | Short Integer | ISRAEL | ISRAEL
| Type | Short Integer
| AssetGroup | Short Integer | ODF
| AssetType | Short Integer
| Number_fiber_interconnections | Double | 48 | 48
| ScrewonTypeConnectors | Short Integer | LC
| Degree_protection | Text | IP55 | IP55
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K05 | K05
| FeederName | Text | MASTER STEEL | MASTER STEEL
| PanelFunction | Short Integer | 2 | 2
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000090/001 | CV917470-000090/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K06 | K06
| FeederName | Text | INCOMER TR1 | INCOMER TR1
| PanelFunction | Short Integer | 1 | 1
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000100/001 | CV917470-000100/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
MV Switch gear | SwitchGearID | Text | SWG-005 | SWG-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| FeederID | Text | K07 | K07
| FeederName | Text | AUXILIARY TR1 | AUXILIARY TR1
| PanelFunction | Short Integer | 2 | 2
| SwitchingDevices | Short Integer | 1 | 1
| Type_of_MV_cable_termination | Short Integer | 2 | 2
| Insulation_Medium | Short Integer | 1 | 1
| Manufacturing_Year | Short Integer | 2017 | 2017
| Serial_Number | Text | CV917470-000090/001 | CV917470-000090/001
| Manufacturer | Text | SIEMENS | SIEMENS
| Year_of_Commissioning | Short Integer | 2017 | 2017
| Country_origin | Text | GERMANY | GERMANY
| Type_Model | Text | 8DA10 | 8DA10
| Altitude_m | Double | 2000 | 2000
| Nominal_voltage_kV | Double | 15 | 15
| Standards | Text | IEC 622271-203 | IEC 622271-203
| Frequency_Hz | Short Integer | 50 | 50
| Rated_voltage_kV | Double | 15 | 15
| Maximum_continu_system_voltage | Double | 24 | 24
| type_protection_relay | Short Integer | ABB-REF 630 | ABB-REF 630 | Should be a Text
| Rated_short_circuit_current | Double | 25 | 25
| Ratedpeak_shortcircuitcurrent | Double | 63 | 63
| RatedBusbar_Current | Double | 1250 | 1250
| Rated_SF6_Pressure_Kpa | Double | 70 | 70
| Minimum_functional_level_for_SF6__KPa_ | Double | 50 | 50
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing | Not existing
Line Bay | Line_Bay_ID | Text | E01 | E01
| Substation_ID | Text | GHNG-005 | GHNG-005
| Line_Bay_Name | Text | MONT KIGALI | MONT KIGALI
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 2 | 2
| Line_Bay_Capacity_MVA | Double | 40 | 40
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 630 | ABB-REF 630
Line Bay | Line_Bay_ID | Text | E02 | E02
| Substation_ID | Text | GHNG-005 | GHNG-005
| Line_Bay_Name | Text | RILIMA | RILIMA
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 2 | 2
| Line_Bay_Capacity_MVA | Double | 40 | 40
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522 | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522 | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 630 | ABB-REF 630
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1 | VT1-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2 | VT1-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3 | VT1-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1 | VT3-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2 | VT3-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3 | VT3-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-1 | VT6-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-2 | VT6-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-3 | VT6-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | ABB | ABB
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 61869-3 | IEC 61869-3
| RatedVoltage_kV1 | Double | 110 | 110
| HighestSystemVoltage_kV | Double | 145 | 145
| TypeofVoltageTransformer | Short Integer | 1 | 1
| AltitudeLevel | Double | 2000 | 2000
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100 | 100
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | 0.1 | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 | 1000
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Double | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650 | 650
| Degree_of_Protection | Text | IP55 | IP55
| Insulation_ | Short Integer | 1 | 1
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-1 | CT1-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double | NA | NA
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400 | 200-400
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866024 | 1HSE8866024
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-2 | CT1-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866025 | 1HSE8866025
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT1-3 | CT1-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866034 | 1HSE8866034
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-1 | CT3-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866012 | 1HSE8866012
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-2 | CT3-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866018 | 1HSE8866018
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT3-3 | CT3-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866009 | 1HSE8866009
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT5-1 | CT5-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866033 | 1HSE8866033
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT5-2 | CT5-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866029 | 1HSE8866029
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
Current Transformer | Manufacturer | Text | ABB | ABB
| Current Transfomer ID | Text | CT5-3 | CT5-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Double | 2015 | 2015
| Standard_Code | Text | IEC61896-2 | IEC61896-2
| RatedOutput_VA | Double | 30 | 30
| Primaryvoltage__kv | Double | 110 | 110
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2 | 1.2
| InsulationLV_kV | Double | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| TemperatureRange | Double | -25°C/+40°C | -25°C/+40°C
| RatedVoltageFactor | Double | NA | NA
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double | 200-400A | 200-400A
| Rated_Secondary_Current | Double | 1A | 1A
| Burden_VA | Double | 30 | 30
| RatedShortTime_CirCurrent_kA | Double | 40 | 40
| Rated_Peak_Short_Cir_Current | Double | 100 | 100
| KneePoint_V | Double
| SerialNumber | Text | 1HSE8866037 | 1HSE8866037
| SF_ALF | Text | 5_20 | 5_20
| LimitsContPrimaryCurrency_A | Double | 1.2 | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275 | 275
| Insulator | Short Integer | 1 | 1
| Degree_of_Protection | Text | IP55 | IP55
| RatedContThermCurrentFactor_A | Double | 1.2 | 1.2
| DurationofShortCircuit_s | Double | 3 | 3
| AltitudeLevel | Double | 2000 | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB1 | CB1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712010 | 1HSB01712010
| Insulation_medium | Short Integer | 1 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | 1 | 1
| RatedVoltage_kV1 | Double | 145 | 145
| HighestSystemVoltage_kV | Double | 170 | 170
| Rated_Frequency | Short Integer | 50 | 50
| Nominal_Current_A | Double | 3150 | 3150
| RatedImpulseWithstandVol | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40kA
| RatedLineChargingCurrent_A | Double | 50 | 50
| RatedShortCircuitMakCurrent_A | Double | 100 | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 | 0.64
| RatedMotorVoltage_VDC | Double | 110 | 110
| RatedSupplyVoltageofAuxCirc | Double | 110 | 110
| RatedSupplyVoltClosOpDevice | Double | 110 | 110
| MaximumBreakingTime_ms | Double | 50 | 50
| MaximumMakingTime_ms | Double | 70 | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | 5 | 5
| OutofPhaseBreakingCurrent | Double | 10 | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1943 | 1943
| TotalMassofInsulatingMed | Double | 11 | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB3 | CB3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712010 | 1HSB01712010
| Insulation_medium | Short Integer | 1 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | 1 | 1
| RatedVoltage_kV1 | Double | 145 | 145
| HighestSystemVoltage_kV | Double | 170 | 170
| Rated_Frequency | Short Integer | 50 | 50
| Nominal_Current_A | Double | 3150 | 3150
| RatedImpulseWithstandVol | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40kA
| RatedLineChargingCurrent_A | Double | 50 | 50
| RatedShortCircuitMakCurrent_A | Double | 100 | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 | 0.64
| RatedMotorVoltage_VDC | Double | 110 | 110
| RatedSupplyVoltageofAuxCirc | Double | 110 | 110
| RatedSupplyVoltClosOpDevice | Double | 110 | 110
| MaximumBreakingTime_ms | Double | 50 | 50
| MaximumMakingTime_ms | Double | 70 | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | 5 | 5
| OutofPhaseBreakingCurrent | Double | 10 | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1943 | 1943
| TotalMassofInsulatingMed | Double | 11 | 11
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ABB | ABB
| CircuitBreakerID | Text | CB5 | CB5
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-100 | IEC 62271-100
| SerialNumber | Text | 1HSB01712010 | 1HSB01712010
| Insulation_medium | Short Integer | 1 | 1
| Class | Text | Class A | Class A
| CommandModel | Short Integer | 3 | 3
| RatedVoltage_kV1 | Double | 145 | 145
| HighestSystemVoltage_kV | Double | 170 | 170
| Rated_Frequency | Short Integer | 50 | 50
| Nominal_Current_A | Double | 3150 | 3150
| RatedImpulseWithstandVol | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| DurationofShortCircuit_s | Double | 3 | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA | 40kA
| RatedLineChargingCurrent_A | Double | 50 | 50
| RatedShortCircuitMakCurrent_A | Double | 100 | 100
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 | 0.64
| RatedMotorVoltage_VDC | Double | 110 | 110
| RatedSupplyVoltageofAuxCirc | Double | 110 | 110
| RatedSupplyVoltClosOpDevice | Double | 110 | 110
| MaximumBreakingTime_ms | Double | 50 | 50
| MaximumMakingTime_ms | Double | 70 | 70
| NumberofTrippingCoils | Short Integer | 1 | 1
| NumberofClosingCoils | Short Integer | 1 | 1
| NumberofOperations | Short Integer | 10000 | 10000
| TemperatureRange | Double | -30°C/+50°C | -30°C/+50°C
| ProtectionClass | Text | IP55 | IP55
| AltitudeLevel | Double | 2000 | 2000
| FirstPoleToClearFactor | Double | 1.5 | 1.5
| Operating_Mechanism | Text | 5 | 5
| OutofPhaseBreakingCurrent | Double | 10 | 10
| Owner | Short Integer | REG | REG
| TotalMassCircuitbreaker_kg | Double | 1943 | 1943
| TotalMassofInsulatingMed | Double | 11 | 11
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1 | Q1-1
| Substation | Text | GHNG-005 | GHNG-005
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250 | 1250
| Operating_Voltage_kV | Double | 110 | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110 | 110
| Auxiliary_Contact_Curr_Rating | Double | 10 | 10
| Motor_Drive | Short Integer | 1 | 1
| Motor_Type | Short Integer | 1 | 1
| Motor_Voltage_V | Double | 110 | 110
| Rated_Peak_Short_Cir_Current | Double | 80 | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1 | Q9-1
| Substation | Text | GHNG-005 | GHNG-005
| Type | Short Integer | 2 | 2
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250 | 1250
| Operating_Voltage_kV | Double | 110 | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110 | 110
| Auxiliary_Contact_Curr_Rating | Double | 10 | 10
| Motor_Drive | Short Integer | 1 | 1
| Motor_Type | Short Integer | 1 | 1
| Motor_Voltage_V | Double | 110 | 110
| Rated_Peak_Short_Cir_Current | Double | 80 | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3 | Q1-3
| Substation | Text | GHNG-005 | GHNG-005
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250 | 1250
| Operating_Voltage_kV | Double | 110 | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110 | 110
| Auxiliary_Contact_Curr_Rating | Double | 10 | 10
| Motor_Drive | Short Integer | 1 | 1
| Motor_Type | Short Integer | 1 | 1
| Motor_Voltage_V | Double | 110 | 110
| Rated_Peak_Short_Cir_Current | Double | 80 | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-3 | Q9-3
| Substation | Text | GHNG-005 | GHNG-005
| Type | Short Integer | 2 | 2
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250 | 1250
| Operating_Voltage_kV | Double | 110 | 110
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110 | 110
| Auxiliary_Contact_Curr_Rating | Double | 10 | 10
| Motor_Drive | Short Integer | 1 | 1
| Motor_Type | Short Integer | 1 | 1
| Motor_Voltage_V | Double | 110 | 110
| Rated_Peak_Short_Cir_Current | Double | 80 | 80
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-5 | Q1-5
| Substation | Text | GHNG-005 | GHNG-005
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | COELME | COELME
| CountryOfManufacturer | Text | ITALY | ITALY
| ManufacturerYear | Short Integer | 2017 | 2017
| Standard_Code | Text | IEC 62271-102 | IEC 62271-102
| Rated_current_A | Double | 1250 | 1250
| Operating_Voltage_kV | Double | 110 | 110
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110 | 110
| Auxiliary_Contact_Curr_Rating | Double | 10 | 10
| Motor_Drive | Short Integer | 1 | 1
| Motor_Type | Short Integer | 1 | 1
| Motor_Voltage_V | Double | 110 | 110
| Rated_Peak_Short_Cir_Current | Double | 80 | 80
Substation/Cabin | AssetGroup | Long | Transmission Substation | 2
| AssetType | Short | Switching Substation | 1
| Substation_Name | Short Integer | GAHANGA | 5
| Substation_ID | Text | GHNG-005 | GHNG-005
| Substation_Total_Capacity_MVA | Double | 40 | 40
| Substation_Voltage_Level_kV | Short Integer | 10 | 10
| SubstationArrangement | Short Integer | 1 | 1
| Number_of_Power_Transformers | Short Integer | 2 | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 1 | 1
| Number_Distribution_Transf | Short Integer | 0 | 0
| Number of auxiliary transformers | Short Integer | 1 | 1
| Standby_Generators | Short Integer | Not | 0
| Busbar_Configuration_HV | Short Integer | 1 | 1
| Number of MV Feeders | Short Integer | 11 | 11
| Number of HV line Bays | Short Integer | 4 | 4
| Number of Trx Bays | Short Integer | 2 | 2
| Configuration_Busbar_MV | Short Integer | 1 | 1
| BuscouplerHV | Short Integer | 0 | 0
| BuscouplerMV | Short Integer | 0 | 0
| Type_of_Busbar_HV | Short Integer | 2 | 2
| Type_of_MV_switchgears | Short Integer | 1 | 1
| Year of Commissioning | Short Integer | 2017 | 2017
| Year_of_upgrade | Short Integer | NA | NA
| Contractor_Name | Text | ELTEL | ELTEL
| Substation_Meter_SN | Text | Not Existing | Not Existing
| Lightning_protection | Short Integer | 1 | 1
| OperatorsLivingHouse | Short Integer | 0 | 0
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-1 | SA1-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-2 | SA1-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA1-3 | SA1-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-1 | SA3-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-2 | SA3-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA3-3 | SA3-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA5-1 | SA5-1
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA5-2 | SA5-2
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA | TRIDELTA
| ArresterID | Text | SA5-3 | SA5-3
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Text | 2017 | 2017
| SerialNumber | Text | Not accesible (Require shutdown) | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099 | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 230 | 230
| MaxContinuousOperatVolt_kV | Double | 102 | 102
| RatedVoltage_kV1 | Double | 110 | 110
| NominalDischargeCurrent_kA | Double | 20 | 20
| Rated_short_circuit_Current | Double | 31.5 | 31.5
| Light_Impulse_Withsand_kV | Double | 650 | 650
| PowerFrequencyWithstandVol | Double | 230 | 230
| RatedContinuousContinuous_kv | Double | 102 | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY | GERMANY
| TypeDischargeCounter | Text | DCC-M2 | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55 | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Type | Short Integer | 1 | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| BatteryFloatingVoltage | Double | 50 | 50
| RatedVoltage | Double | 48 | 48
| TenHrsRatingCapacity | Double | 60 | 60
| One_min_rating_Current_A | Double | 120 | 120
| MaximumVolatge_V | Double | 55.2 | 55.2
| MinimumVoltage_V | Double | 40.8 | 40.8
| MinimumVoltageperCell | Double | 1.02 | 1.02
| NumberofCells | Short Integer | 38 | 38
| BatteryFloatingVoltage | Double | 53.9 | 53.9
| BoostChargingVoltage | Double | 55.8 | 55.8
| FloatChargeCurrent_A | Double | 6.2 | 6.2
| BoostChargeCurrent | Double | 60 | 60
| SelfDischargeat_25oC | Double | 0.7 | 0.7
| TypeofCooling | Text | Natural | Natural
| Charging time (hrs) | Double | 5 | 5
DC Supply 110 VDC Battery | Manufacturer | Text | SAFT (NIFE) | SAFT (NIFE)
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | SWEDEN | SWEDEN
| Model | Text | KL125P | KL125P
| Type | Short Integer | 1 | 1
| Standards_ | Text | IEC 60623 | IEC 60623
| RatedVoltage | Double | 110 | 110
| TenHrsRatingCapacity | Double | 125 | 125
| One_min_rating_Current_A | Double | 100 | 100
| MaximumVolatge_V | Double | 126.5 | 126.5
| MinimumVoltage_V | Double | 93.5 | 93.5
| MinimumVoltageperCell | Double | 1 | 1
| Number_of_cells__No_ | Long Integer | 82 | 82
| BatteryFloatingVoltage | Double | 126 | 126
| BoostChargingVoltage | Double | 136.4 | 136.4
| FloatChargeCurrent_A | Double | 6.2 | 6.2
| BoostChargeCurrent | Double | 100 | 100
| TypeofCooling | Short Integer | Natural | Natural
DC Supply 48 VDC charger | Manufacturer | Text | BENNING | BENNING
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | AUSTRIA | AUSTRIA
| Model | Text | D400G48.0/80 | D400G48.0/80
| Charger_type | Short Integer | 2 | 2
| Standards_ | Short Integer | DIN41773 | DIN41773
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400 | 400
| Rated_InputPower_kVA | Double | 5.53 | 5.53
| DC Output (Kw) | Double | 2.88 | 2.88
| DC_Output_kV | Double | 48 | 48
| Rated_output_Voltage_V | Double | 48 | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5 | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000 | 2000
| Degree_protection_ | Short Integer | 55 | 55
| DCDistributionBoard | Short Integer | 0 | 0
| RatedCurrent_A | Double
| NumberofFeeders | Short Integer
| short_circuit_capacity_breaker | Double
DC Supply 110 VDC charger | Manufacturer | Text | BENNING | BENNING
| Substation_ID | Text | GHNG-005 | GHNG-005
| CountryOfManufacturer | Text | AUSTRIA | AUSTRIA
| Model | Text | D400G104.4/80 | D400G104.4/80
| TypeofOperation | Short Integer | 1 | 1
| Charger_type | Short Integer | 2 | 2
| Standards_ | Text | DIN41773 | DIN41773
| ChargingTime | Double | 5 | 5
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 400 | 400
| Rated_InputPower_kVA | Double | 14.8 | 14.8
| VoltageVariation | Double
| DC_Output_kV | Double | 110 | 110
| TypeofCharging | Text | Float/ Boost | Float/ Boost
| Rated_output_Voltage_V | Double | 110 | 110
| MaximumDC_Voltage_V | Double | 126 | 126
| ConstantVoltageAccuracy | Double
| Rated_DC_output_Current_A | Double | 100A | 100A
| FloatingVoltageRegulatin | Double | 104.4 | 104.4
| EqualisingVoltageRegulatin | Double | 128.8 | 128.8
| Minimum_Insulation_resistance_ | Double | 5 | 5
| TypeofCooling | Short Integer
| Ambient_temperature | Double
| Altitude_m | Double | 1000 | 1000
| Total_Weight_Charger_kg | Double | 250 | 250
| Degree_protection_ | Short Integer | 55 | 55
| RatedCurrent_A | Double | 100 | 100
| ShortCircuitStrength_kA_sec | Double
| BusbarMaterial | Short Integer
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE | FRANCE
| Type | Text | REASON DR60 | REASON DR60
| Standards | Text | IEC61850 | IEC61850
| Arrangement | Short Integer | 2 | 2
| VT_CT_Connection | Short Integer | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| Nominal_input_current_A | Double | 1 | 1
| Nominal_voltage_Vdc | Double | 110 | 110
| Power_consumption_VA | Double | 150 | 150
| NumberofAnalogInputs | Short Integer | 32 | 32
| NumberofBinaryInputs | Short Integer | 96 | 96
| NumberofBinaryOutputs | Short Integer | 48 | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | MONT KIGALI | MONT KIGALI
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | ELTEL | ELTEL
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 6 | 6
| ShieldWire | Short Integer | 1 | 1
| ConductorType | Short Integer | 1 | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 8.4 | 8.4
| CurrentCarryingCapacity | Double | 40 | 40
| NominalBreakingLoad_KN | Double | 130 | 130
| MaxElectricResitance | Double | 0.119 | 0.119
| PositiveSequenceReactance | Double | 0.427 | 0.427
| PositiveSequenceResistance | Double | 0.123 | 0.123
| ZeroSequenceResistance | Double | 0.327 | 0.327
| ZeroSequenceReactance | Double | 1.119 | 1.119
| ZeroSequenceCapacitance | Double | 0.011 | 0.011
| PositiveSequenceCapacitance | Double | 0.0066 | 0.0066
High Voltage Line | Name | Text | BUGESERA | BUGESERA
| Year_of_commisioning | Short Integer | 2017 | 2017
| ContractorName | Text | ELTEL | ELTEL
| Manufacturer | Text | Not known | Not known
| Voltage_Level_kV | Short Integer | 2 | 2
| CondustorSize | Short Integer | 6 | 6
| ShieldWire | Short Integer | 1 | 1
| ConductorType | Short Integer | 1 | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 8.4 | 8.4
| CurrentCarryingCapacity | Double | 40 | 40
| NominalBreakingLoad_KN | Double | 130 | 130
| MaxElectricResitance | Double | 0.119 | 0.119
| PositiveSequenceReactance | Double | 0.427 | 0.427
| PositiveSequenceResistance | Double | 0.123 | 0.123
| ZeroSequenceResistance | Double | 0.327 | 0.327
| ZeroSequenceReactance | Double | 1.119 | 1.119
| ZeroSequenceCapacitance | Double | 0.011 | 0.011
| PositiveSequenceCapacitance | Double | 0.0066 | 0.0066
Transformer Bay | Trx_Bay_ID | Text | E05 | E05
| Substation_ID | Text | GHNG-005 | GHNG-005
| Trx_Bay_Name | Text | TRANSFORMER 1 | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing | Not existing
| VoltageLevel_kV | Long Integer | 2 | 2
| Trx_Bay_Capacity_MVA | Double | 20 | 20
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_Trx_Differencial_relay | Text | SIEMENS-7UT612 | SIEMENS-7UT612
| Type_of_Back_up_relay | Text | Included in 7UT612 | Included in 7UT612
| Type_of_BCU_Bay_control_unit | Text | ABB - REF630 | ABB - REF630
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SIEMENS | SIEMENS
| CircuitBreakerID | Text | CB-MV1 | CB-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 3HA49 | 3HA49
| Standard | Text | IEC 62271-200 | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | 1 | 1
| ArcQuenchingMedium | Short Integer | 2 | 2
| Number_phases | Long Integer | 3 | 3
| RatedVoltage_kV1 | Double | 15 | 15
| MaxContinuousOperatVolt_kV | Double | 24 | 24
| RatedImpulseWithstandVol | Double | 95 | 95
| PowerFrequencyWithstandVol | Double | 38 | 38
| Rated_Frequency | Short Integer | 50 | 50
| Rated_short_time_withstand_current__kA_ | Text | 25 | 25
| Rated_Peak_Short_Cir_Current | Double | 63 | 63
| RatedNormalCurrent_A | Double | 1250 | 1250
| RatedShortCircuitBreakCur_kA | Double | 25 | 25
| RatedShortCircuitMakCurrent_A | Double | 63 | 63
| RatedCableChargingBreakingCur | Double | 50 | 50
| MaximumCApacitivBreakingCur | Double | 875 | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60 | 60
| DeadTime_ms | Double | 300 | 300
| BreakTime_ms | Double | 85 | 85
| MakeTime_ms | Double | 70 | 70
| ArcingTime_ms | Double | 15 | 15
| AtRAtedContinuousCurrent | Double
| AtRAtedBreakingCurrent | Double
| NumberofNO | Short Integer | 8 | 8
| NumberofNc | Short Integer | 8 | 8
| RatedMotorVoltage_VDC | Double | 110 | 110
| NumberofMakingCoils | Short Integer | 1 | 1
| NumberofTrippingCoils | Short Integer | 1 | 1
| Volatge_VDC | Double | 110 | 110
| PowerSupply | Short Integer | 110 | 110
| HandOperatingFacility | Short Integer | 1 | 1
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV1 | CT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 24kV | 24kV
| Rated_Frequency | Short Integer | 50Hz | 50Hz
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double
| Rated_Secondary_Current | Double | 1 | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10VA | 10
| RatedShortTimeWithstandCur | Double | 25kA | 25
| Rated_Peak_Short_Cir_Current | Double | 63kA | 63
| RatedImpulseWithstandVol | Double | 95kV | 95
| LimitsContPrimaryCurrency_A | Double | 2400 | 2400
Indoor Current Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV3 | CT-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Type__model | Text | 4MT74XD | 4MT74XD
| Standard | Text | IEC 61869-1 | IEC 61869-1
| RatedVoltage_kV1 | Double | 24 | 24
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| NumberofCores | Short Integer | 2 | 2
| Rated_Primary_Current_A | Double
| Rated_Secondary_Current | Double | 1 | 1
| AccuracyClass | Text | Cl 0.5-5P20 | Cl 0.5-5P20
| Burden_VA | Double | 10 | 10
| RatedShortTimeWithstandCur | Double | 25 | 25
| Rated_Peak_Short_Cir_Current | Double | 63 | 63
| RatedImpulseWithstandVol | Double | 95 | 95
| LimitsContPrimaryCurrency_A | Double | 768 | 768
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV1 | VT-MV1
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38 | 38
| RatedImpulseWithstandVol | Double | 95 | 95
| RatedPrimaryVoltage_kV | Double | 15 | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60 | 60
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV3 | VT-MV3
| CountryOfManufacturer | Text | GERMANY | GERMANY
| Standard | Text | IEC 61869-1 | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1 | 1
| PowerFrequencyWithstandVol | Double | 38 | 38
| RatedImpulseWithstandVol | Double | 95 | 95
| RatedPrimaryVoltage_kV | Double | 15 | 15
| Rated_secondary_voltage_winding_1__V_ | Text | 100 | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100 | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5 | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P | Cl 3P
| RatedOutput_VA | Double | 60 | 60
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-005 | TSP-CPR-1-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| Bay_ID | Text | E01 | E01
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5 | 2.5
| Max_height_mm | Double | 2000 | 2000
| MaxWidth_mm | Double | 1500 | 1500
| MaxDepth | Double | 2500 | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1 | 1
| Rated_Voltage | Double | 100 | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110 | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-005 | TSP-CPR-1-005
| Substation_ID | Text | GHNG-005 | GHNG-005
| Bay_ID | Text | E03 | E03
| ProtectionClass | Text | IP 65 | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5 | 2.5
| Max_height_mm | Double | 2000 | 2000
| MaxWidth_mm | Double | 1500 | 1500
| MaxDepth | Double | 2500 | 2500
| FrontdoorMaterial | Text | Steel | Steel
| Colouring | Text | RAL 7035 | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522 | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E03 | E03
| Substatoin_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Rated_Current | Double | 1 | 1
| Rated_Voltage | Double | 100 | 100
| Number_Phases | Short Integer | 3 | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110 | 110
| QtyofOutputRelaysorContact | Short Integer | 23 | 23
| QtyofLEDsforIndications | Short Integer | 14 | 14
| System_Interface | Text | Fiber optic | Fiber optic
Transformer Protection | RelayType | Text | SIEMENS-7UT612 | SIEMENS-7UT612
| Bay_ID | Text | E05 | E05
| Substatoin_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50Hz
| DC_Supply_V | Double | 110V | 110V
| FronSerialInterfaceCom | Text | RS485 | RS485
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E01 | E01
| Substatoin_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50Hz
| Phase current (A) |  | 1-5A | 1A
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110V DC
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522 | Included in SIEMENS-7SD522
| Bay_ID | Text | E03 | E03
| Substatoin_ID | Text | GHNG-005 | GHNG-005
| Manufacturer | Text | SIEMENS | SIEMENS
| Country_manufacturer_ | Text | GERMANY | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50Hz
| Phase current (A) |  | 1-5A | 1A
| Phase to phase voltage (V) |  | 100-110V AC | 100
| Auxiliary voltage (V DC) |  | 110V DC | 110
| System_Interface | Text | Fiber optic | Fiber optic
| Connection | Text | ST | ST
| Protocol | Text | IEC 60870-5-103 | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Not existing | Not existing
| Substation_ID | Text | Not existing | Not existing
| Standby_Generator_ID | Text | Not existing | Not existing
| CountryOfManufacturer | Text | Not existing | Not existing
| Mode_Operation | Short Integer | Not existing | Not existing
| Model | Text | Not existing | Not existing
| Type_Assembly | Short Integer | Not existing | Not existing
| Arrangement | Short Integer | Not existing | Not existing
| Phases | Short Integer | Not existing | Not existing
| RatedOuptuPower_kVA | Double | Not existing | Not existing
| RatedVoltage | Double | Not existing | Not existing
| RatedCurrent_A | Double | Not existing | Not existing
| PowerFactor | Double | Not existing | Not existing
| CouplingofEngine | Text | Not existing | Not existing
| FuelLevelEmissionPerm | Double | Not existing | Not existing
| DieselEngineType | Text | Not existing | Not existing
| Governor | Text | Not existing | Not existing
| GobernorBrand | Text | Not existing | Not existing
| RatedPower_kVA_kW | Double | Not existing | Not existing
| CompressionRatio_ | Text | Not existing | Not existing
| NoofCylinder | Short Integer | Not existing | Not existing
| Speed_RPM | Double | Not existing | Not existing
| Applicable_Standard | Text | Not existing | Not existing
| SpeedREgulation | Short Integer | Not existing | Not existing
| Fuel_Tank_Capacity | Double | Not existing | Not existing
| Cooling_System | Short Integer | Not existing | Not existing
| NoiseatFullLoad | Double | Not existing | Not existing
| LubricationOilConsumption | Double | Not existing | Not existing
| Ambient_temperature | Double | Not existing | Not existing
| Protection index | Text | Not existing | Not existing
| MethodofStarting | Text | Not existing | Not existing
| Voltage_VDC | Double | Not existing | Not existing
| Power_kW | Double | Not existing | Not existing
| Battery_Capacity_Ah | Double | Not existing | Not existing
| BatteryType | Text | Not existing | Not existing
| BrandandModelofBattery | Text | Not existing | Not existing
| Frequency_Hz | Short Integer | Not existing | Not existing
| VoltageRegulationMode | Short Integer | Not existing | Not existing
| Total_Weight | Double | Not existing | Not existing