## GIFURWE SUBSTATION
GIFURWE
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-024
| PowerPlantID | Text | NA
| Substation_ID | Text | GFRW-024
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | DACHI ELECTRIC
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2017
| Year_commissioning | Short Integer | 2017
| Owner | Short Integer | REG |  | REG (This Should be a Text or create a Domain code)
| Rated_Power_MVA | Double | 10 MVA
| Primaryvoltage__kv | Double | 110 kV
| Secondaryvoltage__kv | Double | 30kV
| TertiaryCurrent_A | Short Integer | NA | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 52.5A
| SecondaryCurrent_A | Double | 192.6A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | YNd11 | 19
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 9.95%
| NoLoadCurr_Percentage | Double | 10%
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2
| No_Load_losses | Double | 12.257kW
| LoadLosses | Double | 72.19kW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 75dB
| NumberOfTappingPosition | Short Integer | 17
| TapChangerType | Short Integer | Onload | 1
| TapChangerModel | Text | UV III 400Y-76-10193W
| TappingRange | Double | 110±16% | 110±16% | 110±16% (This can not be a single Number because it is plus/minus)
| Tap_changer_manufacturer | Text | MR
| Tap_changer_country_orgin_ | Text | GERMANY
| TapChangerManufacturingDate | Short Integer | 2017
| SerialNumber | Text | 1771935
| Barcode | Text | NA
| TotalWeight | Double | 32535kg |  | Unit in kg missing
| WeightOfActivePart | Double | Not provided |  | Unit in kg missing
| WeightOfOil | Double | 10070kg |  | Unit in kg missing
| WeightOfUpperTank | Double | Not provided |  | Unit in kg missing
| TransportationOfWeight_N2 | Double | Not provided |  | Unit in kg missing
| Height | Double | Not provided |  | unit in m missing
| Depth | Double | Not provided |  | unit in m missing
| Width | Double | Not provided |  | unit in m missing
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | AUX TR-1-024
| PowerPlantID | Text | NA
| Substation_ID | Text | GFRW-024
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR2 | 0
| Manufacturer | Text | DACHI ELECTRIC
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2017
| Owner | Short Integer | REG | 1
| Primaryvoltage__kv | Double | 30kV
| Secondaryvoltage__kv | Double | 0.4kV
| TertiaryCurrent_A | Short Integer | NA | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 3.081A
| SecondaryCurrent_A | Double | 231.2A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | ZNyn11 | 20 | YZn5
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | OUTDOOR | 0
| PercentageImpedance | Double | 4.3%
| No_Load_losses | Double | 2kW |  | Unit missing in kWatt
| LoadLosses | Double | 0.5KW |  | Unit missing in kWatt
| AltitudeLevel | Double | 2000m |  | Unit missing in m
| Noiselevel_db | Double | 55dB
| NumberOfTappingPosition | Short Integer | 3
| Standard_Code | Text | IEC 60076
| Tap_changer | Short Integer | OFF LOAD
| VoltageVariationRange1 | text | 30kV±2.5%
| Tap_changer_manufacturer | Text | DACHI ELECTRIC
| Tap_changer_country_orgin_ | Text | CHINA
| TapChangerManufacturingDate | Short Integer | 2012
| SerialNumber | Text | Incorporated in Transformer
| Barcode | Text | NA
| TotalWeight | Double | 3330kg |  | Unit in kg missing
| WeightOfActivePart | Double | Not provided |  | Unit in kg missing
| WeightOfOil | Double | 980kg |  | Unit in kg missing
| WeightOfUpperTank | Double | Not provided |  | Unit in kg missing
| TransportationOfWeight_N2 | Double | Not provided |  | Unit in kg missing
| WeightOfAccessories | Double | Not provided |  | Unit in kg missing
| LV_CB_A | Short Integer | 400A
| Earthing_Switch | Short Integer | NA
| Notes | Text | NA
| Branch | text | NA
| Year_commissioning | Short Integer | 2017
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | GFRW-024
| Busbar_HV_ID | Text | Not Existing
| Number_of_Busbar_HV | Short Integer | Not Existing
| Number_of_Busbar_MV | Short Integer | Not Existing
| Type_of_Busbar | Short Integer | Not Existing |  | Not Existing (T-off Subatation)
| Phase_sequence | Short Integer | Not Existing | 7
| Busbar_Material | Short Integer | Not Existing | 3
| Barcode | Short Integer | Not Existing
| Operating_Voltage_Level_kV | Double | Not Existing
| Short_circuit_current_kA | Double | Not Existing
| Nominal_Current_A | Double | Not Existing
| Frequency_Hz | Short Integer | Not Existing | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-024
| Substation_ID | Text | GFRW-024
| FeederID | Text | H01
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017
| Serial_Number | Text | 16V1804
| Manufacturer | Text | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2017
| Country_origin | Text | CHINA
| Type_Model | Text | GSW
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 615
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-024
| Substation_ID | Text | GFRW-024
| FeederID | Text | H02
| FeederName | Text | GAKENKE
| PanelFunction | Short Integer | Line feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017
| Serial_Number | Text | 16V1803
| Manufacturer | Text | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2017
| Country_origin | Text | CHINA
| Type_Model | Text | GSW
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 615
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-024
| Substation_ID | Text | GFRW-024
| FeederID | Text | H03
| FeederName | Text | NTARUKA
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017
| Serial_Number | Text | 16V1805
| Manufacturer | Text | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2017
| Country_origin | Text | CHINA
| Type_Model | Text | GSW
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 615
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | No | 1
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-024
| Substation_ID | Text | GFRW-024
| FeederID | Text | H04
| FeederName | Text | KIRAMBO
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017
| Serial_Number | Text | 16V1806
| Manufacturer | Text | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2017
| Country_origin | Text | CHINA
| Type_Model | Text | GSW
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 615
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | No | 1
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-024
| Substation_ID | Text | GFRW-024
| FeederID | Text | H05
| FeederName | Text | SPARE
| PanelFunction | Short Integer | Line feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2017
| Serial_Number | Text | 16V1807
| Manufacturer | Text | SCHNEIDER
| Year_of_Commissioning | Short Integer | 2017
| Country_origin | Text | CHINA
| Type_Model | Text | GSW
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 615 |  | REF 630 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | No | 1
| Meter_number___if_yes_ | Text | Not existing
Line Bay | Line_Bay_ID | Text | E01
| Substation_ID | Text | GFRW-024
| Line_Bay_Name | Text | MUKUNGWA-RULINDO
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 6
| Line_Bay_Capacity_MVA | Double | 40MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | Not existing
| Type_of_Distance_relay | Text | Not existing
| Type_of_Back_up_relay | Text | Not existing
| Type_of_BCU_Bay_control_unit | Text | Not existing
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1
| Substation_ID | Text | GFRW-024
| Manufacturer | Text | SIEYUAN
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2016
| Standard_Code | Text | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000 |  | Unit in m is missing
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2
| Substation_ID | Text | GFRW-024
| Manufacturer | Text | SIEYUAN
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2016
| Standard_Code | Text | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000 |  | Unit in m is missing
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3
| Substation_ID | Text | GFRW-024
| Manufacturer | Text | SIEYUAN
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2016
| Standard_Code | Text | IEC 60044-1
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000 |  | Unit in m is missing
| Winding_Material | Short Integer | 1 | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 650kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | SIEYUAN
| Current Transfomer ID | Text | CT1-1
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2016
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 50-100A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA
| KneePoint_V | Double
| SerialNumber | Text | 11164537
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120A
| PowerFrequencyTestVoltage_kV | Double | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | SIEYUAN
| Current Transfomer ID | Text | CT1-2
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2016
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 50-100A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA
| KneePoint_V | Double
| SerialNumber | Text | 11164539
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120A
| PowerFrequencyTestVoltage_kV | Double | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | SIEYUAN
| Current Transfomer ID | Text | CT1-3
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2016
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 50-100A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA
| KneePoint_V | Double
| SerialNumber | Text | 11164538
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120A
| PowerFrequencyTestVoltage_kV | Double | 275
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | SIEYUAN
| CircuitBreakerID | Text | CB1
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2016
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | DH160449
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three pole | 1
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.6MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C |  | This should be a Text -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG |  | REG This should be a text or create a Domain code
| TotalMassCircuitbreaker_kg | Double | 1700kg
| TotalMassofInsulatingMed | Double | 8kg |  | Unit in kg is missing
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1
| Substation | Text | GFRW-024
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 1
| Manufacturer | Text | SIEYUAN
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2017
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | Yes | 0
| Auxiliary_Contact_vol_Rating | Double | 110V
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | Yes | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V
| Rated_Peak_Short_Cir_Current | Double | 80kA
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | Substation_Name | Short Integer | GIFURWE
| Substation_ID | Text | GFRW-024
| Substation_Total_Capacity_MVA | Double | 10MVA
| Substation_Voltage_Level_kV | Short Integer | 110/30kV | 13
| SubstationArrangement | Short Integer | T-off Substaion | 1
| Number_of_Power_Transformers | Short Integer | 1
| Numbe_of_Earthing_Transfomer | Short Integer | 0
| Number_Distribution_Transf | Short Integer | 0
| Number of auxiliary transformers | Short Integer | 1 | 1 | This Should allow to add a Number of Aux TR not the chose Yes or Not
| Standby_Generators | Short Integer | No
| Busbar_Configuration_HV | Short Integer | No Busbar (T-off Substation) | 1
| Number of MV Feeders | Short Integer | 6
| Number of HV line Bays | Short Integer | 0
| Number of Trx Bays | Short Integer | 1
| Configuration_Busbar_MV | Short Integer | Single busbar | 1
| BuscouplerHV | Short Integer | No | 0
| BuscouplerMV | Short Integer | No | 0
| Type_of_Busbar_HV | Short Integer | Not Existing | 2
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 1987
| Year_of_upgrade | Short Integer | 1987 & 2017
| Contractor_Name | Text | FORCE DE L'EST - GTME - SIEYUAN
| Substation_Meter_SN | Text | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1
Lightning Arrester | Manufacturer | Short Integer | NANYANG JINGUAN
| ArresterID | Text | SA1-1
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2016
| SerialNumber | Text | 6120994B
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | Yes | 1
| manufacturer_Disch_Counter | Text | ASEA
| Country_orgin_Dis_Counter | Text | SWEDEN
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | NANYANG JINGUAN
| ArresterID | Text | SA1-2
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2016
| SerialNumber | Text | 6121001B
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | Yes | 1
| manufacturer_Disch_Counter | Text | ASEA
| Country_orgin_Dis_Counter | Text | SWEDEN
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | NANYANG JINGUAN
| ArresterID | Text | SA1-3
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2016
| SerialNumber | Text | 6120985B
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | Yes | 1
| manufacturer_Disch_Counter | Text | ASEA
| Country_orgin_Dis_Counter | Text | SWEDEN
| TypeDischargeCounter | Text
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | CHANGHONG
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60623
| BatteryFloatingVoltage | Double | 50V |  | Unit in V is missing
| RatedVoltage | Double | 48V |  | Unit in V is missing
| TenHrsRatingCapacity | Double | 60Ah |  | Unit in Ah is missing
| One_min_rating_Current_A | Double | 120A
| MaximumVolatge_V | Double | 55.2V
| MinimumVoltage_V | Double | 40.8V
| MinimumVoltageperCell | Double | 1.02V
| NumberofCells | Short Integer | 42
| BatteryFloatingVoltage | Double | 53.9V
| BoostChargingVoltage | Double | 55.8V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 60A
| SelfDischargeat_25oC | Double | 0.7
| TypeofCooling | Text | Natural
| Charging time (hrs) | Double | 5h
DC Supply 110 VDC Battery | Manufacturer | Text | CHANGHONG
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | CHINA
| Model | Text | FNC 90L (KL 90P)
| Type | Short Integer | NiCd
| Standards_ | Text | IEC 60623
| RatedVoltage | Double | 110V
| TenHrsRatingCapacity | Double | 100Ah |  | Unit in Ah is missing
| One_min_rating_Current_A | Double | 100A
| MaximumVolatge_V | Double | 126.5V
| MinimumVoltage_V | Double | 93.5V
| MinimumVoltageperCell | Double | 1V
| Number_of_cells__No_ | Long Integer | 92
| BatteryFloatingVoltage | Double | 126V
| BoostChargingVoltage | Double | 136.4V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 100A
| TypeofCooling | Short Integer | Natural
DC Supply 48 VDC charger | Manufacturer | Text | AEG
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | GERMANY
| Model | Text | POWER SOLUTIONS
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 5.53kVA
| DC Output (Kw) | Double | 2.88kW
| DC_Output_kV | Double | 48V |  | Unit in should be in V not in kV
| Rated_output_Voltage_V | Double | 48V
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΩ
| OperatingConditions | Text
| Altitude_m | Double | 2000m
| Degree_protection_ | Short Integer | IP55 | 55
| DCDistributionBoard | Short Integer | No | 0
| RatedCurrent_A | Double
| NumberofFeeders | Short Integer
| short_circuit_capacity_breaker | Double
DC Supply 110 VDC charger | Manufacturer | Text | AEG Power Supply Systems GmbH
| Substation_ID | Text | GFRW-024
| CountryOfManufacturer | Text | GERMANY
| Model | Text | POWER SOLUTIONS
| TypeofOperation | Short Integer | Parallel_standby
| Charger_type | Short Integer | Thyristor controlled
| Standards_ | Text | DIN41773
| ChargingTime | Double | 5h
| Frequency_Hz | Short Integer | 50Hz
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 17.3kVA
| VoltageVariation | Double |  |  | ±5% This should be a Text
| DC_Output_kV | Double | 110V
| TypeofCharging | Text | Float/ Boost
| Rated_output_Voltage_V | Double | 110V
| MaximumDC_Voltage_V | Double | 126V
| ConstantVoltageAccuracy | Double |  |  | ±10% V This should be a Text
| Rated_DC_output_Current_A | Double | 100A
| FloatingVoltageRegulatin | Double | 104.4
| EqualisingVoltageRegulatin | Double | 128.8
| Minimum_Insulation_resistance_ | Double | 5
| TypeofCooling | Short Integer | Natural self-ventilating |  | Natural self-ventilating, Others (Domain code not given)
| Ambient_temperature | Double | 0°C to +40°C |  | This should be a Text 0°C to +40°C
| Altitude_m | Double | 1000
| Total_Weight_Charger_kg | Double | 340kg
| Degree_protection_ | Short Integer | IP55
| RatedCurrent_A | Double | 100A
| ShortCircuitStrength_kA_sec | Double
| BusbarMaterial | Short Integer |  |  | Copper tin-plate (No domain code is given)
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE
| Type | Text | REASON DR60
| Standards | Text | IEC61850
| Arrangement | Short Integer | 2 | 2
| VT_CT_Connection | Short Integer | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| Nominal_input_current_A | Double | 1 |  | This can be programmed to accept 5A also
| Nominal_voltage_Vdc | Double | 110
| Power_consumption_VA | Double | 150
| NumberofAnalogInputs | Short Integer | 32
| NumberofBinaryInputs | Short Integer | 96
| NumberofBinaryOutputs | Short Integer | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | MUKUNGWA-RULINDO
| Year_of_commisioning | Short Integer | 1959
| ContractorName | Text | FORCE DE L'EST
| Manufacturer | Text | Not known
| Voltage_Level_kV | Short Integer | 110kV | 110
| CondustorSize | Short Integer | 150/25 | 6 | 240/40 Type has to Domain codes 3&6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 19.6Km
| CurrentCarryingCapacity | Double | 40MW |  | Unit in MW is missing
| NominalBreakingLoad_KN | Double | 130KN
| MaxElectricResitance | Double | 0.1937(Ω/km) |  | Unit in (Ώ/km)is missing
| PositiveSequenceReactance | Double | 0.437(Ω/km) |  | Unit in (Ώ/km)is missing
| PositiveSequenceResistance | Double | 0.231(Ω/km) |  | Unit in (Ώ/km)is missing
| ZeroSequenceResistance | Double | 0.554(Ω/km) |  | Unit in (Ώ/km)is missing
| ZeroSequenceReactance | Double | 1.430(Ω/km) |  | Unit in (Ώ/km)is missing
| ZeroSequenceCapacitance | Double | 0.01(µF) |  | Unit in (Ώ/km)is missing
| PositiveSequenceCapacitance | Double | 0.0063(µF) |  | Unit in (Ώ/km)is missing
Transformer Bay | Trx_Bay_ID | Text | E01
| Substation_ID | Text | GFRW-024
| Trx_Bay_Name | Text | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 10MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SCHENEIDER-MICOM P632
| Type_of_Back_up_relay | Text | Included in MICOM P632
| Type_of_BCU_Bay_control_unit | Text | SCHNEIDER - MICOM P139
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SCHNEIDER
| CircuitBreakerID | Text | CB-MV1
| CountryOfManufacturer | Text | CHINA
| Type__model | Text | WS-G36-25-12
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 1250A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SCHNEIDER
| CircuitBreakerID | Text | CB-MV1
| CountryOfManufacturer | Text | CHINA
| Type__model | Text | WS-G36-25-12
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 1250A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | SCHNEIDER
| CurrentTransfomer_ID | Text | CT-MV1
| CountryOfManufacturer | Text | CHINA
| Type__model | Text | CHA 250/81 CA
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 1 |  | Unit in A is missing
| AccuracyClass | Text | Cl 0.5-5P20
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 170kV
| LimitsContPrimaryCurrency_A | Double | 480
Indoor Current Transformer | Manufacturer | Text | SCHNEIDER
| CurrentTransfomer_ID | Text | CT-MV3
| CountryOfManufacturer | Text | CHINA
| Type__model | Text | CHA 250/81 CA
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 1 |  | Unit in A is missing
| AccuracyClass | Text | Cl 0.5-5P20
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA |  | Unit in kA is missing
| Rated_Peak_Short_Cir_Current | Double | 63kA |  | Unit in kA is missing
| RatedImpulseWithstandVol | Double | 170kV |  | Unit in kV is missing
| LimitsContPrimaryCurrency_A | Double | 240
Indoor Voltage Transformer | Manufacturer | Text | SCHNEIDER
| VoltageTransfomer_ID | Text | VT-MV1
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | VGM 36 H
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70kV |  | Unit in kV is missing
| RatedImpulseWithstandVol | Double | 170kV |  | Unit in kV is missing
| RatedPrimaryVoltage_kV | Double | 30kV
| Rated_secondary_voltage_winding_1__V_ | Text | 100V
| Rated_secondary_voltage_winding_2__V_ | Text | 100V
| Accuracy_class__measuring_ | Text | Cl 0.5 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 60VA
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | SCHNEIDER
| VoltageTransfomer_ID | Text | VT-MV3
| CountryOfManufacturer | Text | CHINA
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | VGM 36 H
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70kV |  | Unit in kV is missing
| RatedImpulseWithstandVol | Double | 170kV |  | Unit in kV is missing
| RatedPrimaryVoltage_kV | Double | 30kV
| Rated_secondary_voltage_winding_1__V_ | Text | 100V
| Rated_secondary_voltage_winding_2__V_ | Text | 100V
| Accuracy_class__measuring_ | Text | Cl 0.5 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 60VA
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-024
| Substation_ID | Text | GFRW-024
| Bay_ID | Text | E01
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5mm |  | Unit in mm is missing
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E01
| Substatoin_ID | Text | GFRW-024
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1
| Rated_Voltage | Double | 100
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Transformer Protection | RelayType | Text | ABB RET630
| Bay_ID | Text | E04
| Substatoin_ID | Text | GFRW-024
| Manufacturer | Text | ABB
| Country_manufacturer_ | Text | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E01
| Substatoin_ID | Text | GFRW-024
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Not existing
| Substation_ID | Text | GFRW-024
| Standby_Generator_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Mode_Operation | Short Integer | Not existing
| Model | Text | Not existing
| Type_Assembly | Short Integer | Not existing
| Arrangement | Short Integer | Not existing
| Phases | Short Integer | Not existing
| RatedOuptuPower_kVA | Double | Not existing
| RatedVoltage | Double | Not existing
| RatedCurrent_A | Double | Not existing
| PowerFactor | Double | Not existing
| CouplingofEngine | Text | Not existing
| FuelLevelEmissionPerm | Double | Not existing
| DieselEngineType | Text | Not existing
| Governor | Text | Not existing
| GobernorBrand | Text | Not existing
| RatedPower_kVA_kW | Double | Not existing
| CompressionRatio_ | Text | Not existing
| NoofCylinder | Short Integer | Not existing
| Speed_RPM | Double | Not existing
| Applicable_Standard | Text | Not existing
| SpeedREgulation | Short Integer | Not existing
| Fuel_Tank_Capacity | Double | Not existing
| Cooling_System | Short Integer | Not existing
| NoiseatFullLoad | Double | Not existing
| LubricationOilConsumption | Double | Not existing
| Ambient_temperature | Double | Not existing
| Protection index | Text | Not existing
| MethodofStarting | Text | Not existing
| Voltage_VDC | Double | Not existing
| Power_kW | Double | Not existing
| Battery_Capacity_Ah | Double | Not existing
| BatteryType | Text | Not existing
| BrandandModelofBattery | Text | Not existing
| Frequency_Hz | Short Integer | Not existing
| VoltageRegulationMode | Short Integer | Not existing
| Total_Weight | Double | Not existing